## Sheet1
| Spec Section Number | Spec Sub Section | Submittal Type | Predicted Labels | Submittal Description
6 | 42200 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : For the following: 1. Masonry Units: Show sizes, profiles, coursing, and locations of special shapes. 2. Reinforcing Steel: Detail bending, lap lengths, and placement of unit masonry reinforcing bars. Comply with ACI 315. Show elevations of reinforced walls. 3. Fabricated Flashing: Detail corner units, end-dam units, and other special applications.
17 | 42200 | 1.6-C | Mix Design | Mix Design | Mix Designs : For each type of mortar and grout. Include description of type and proportions of ingredients. 1. Include test reports for mortar mixes required to comply with property specification. Test according to ASTM C109/C109M for compressive strength, ASTM C1506 for water retention, and ASTM C91/C91M for air content. 2. Include test reports, according to ASTM C1019, for grout mixes required to comply with compressive strength requirement.
20 | 54000 | 1.4-A | Product Data | Product Data | Product Data : For the following: 1. Cold-formed steel framing materials. 2. Interior non-load-bearing wall framing. 3. Vertical deflection clips. 4. Single deflection track. 5. Drift clips. 6. Soffit framing. 7. Power-actuated anchors.
27 | 54000 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : - 1. Include layout, spacings, sizes, thicknesses, and types of cold-formed steel framing; fabrication; and fastening and anchorage details, including mechanical fasteners. 2. Indicate reinforcing channels, opening framing, supplemental framing, strapping, bracing, bridging, splices, accessories, connection details, and attachment to adjoining work.
39 | 55000 | 1.4-A | Product Data | Product Data | Product Data : For the following: 1. Nonslip aggregates and nonslip-aggregate surface finishes. 2. Fasteners. 3. Shop primers. 4. Shrinkage-resisting grout. 5. Prefabricated building columns. 6. Slotted channel framing. 7. Alternating tread devices. 8. Metal bollards. 9. Abrasive metal nosings.
48 | 55000 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : Show fabrication and installation details. Include plans, elevations, sections, and details of metal fabrications and their connections. Show anchorage and accessory items. Provide Shop Drawings for the following: 1. Steel framing and supports for ceiling-hung toilet compartments. 2. Steel framing and supports for operable partitions. 3. Steel framing and supports for overhead doors. 4. Steel framing and supports for countertops. 5. Steel framing and supports for laboratory equipment. 6. Elevator machine beams, hoist beams and divider beams. 7. Steel shapes for supporting elevator door sills. 8. Prefabricated building columns. 9. Shelf angles. 10. Alternating tread devices. 11. Metal floor plate and supports. 12. Elevator pit sump covers. 13. Miscellaneous steel trim including steel angle corner guards and loading-dock edge angles. 14. Metal bollards. 15. Abrasive metal nosings.
70 | 55119 | 1.4-A | Product Data | Product Data | Product Data : For metal grating stairs and the following: 1. Gratings. 2. Shop primer products. 3. Grout.
73 | 55119 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, details, and attachment to other work. 2. Indicate sizes of metal sections, thickness of metals, profiles, holes, and field joints. 3. Include plan at each level. 4. Indicate locations of anchors, weld plates, and blocking for attachment of wall-mounted handrails.
78 | 55213 | 1.4-A | Product Data | Product Data | Product Data : - 1. Manufacturer's product lines of mechanically connected railings. 2. Fasteners. 3. Post-installed anchors. 4. Handrail brackets. 5. Shop primer. 6. Intermediate coats and topcoats. 7. Nonshrink, nonmetallic grout. 8. Anchoring cement. 9. Metal finishes. 10. Paint products.
88 | 55213 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : Include plans, elevations, sections, details, and attachments to other work.
97 | 57313 | 1.5-A | Product Data | Product Data | Product Data : - 1. Glass products. 2. Glazing cement and accessories for structural glass railings. 3. Sealant and accessories for structural glass railings. 4. Fasteners. 5. Nonshrink, nonmetallic grout. 6. Anchoring cement.
103 | 57313 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : Include plans, elevations, sections, and attachment details.
118 | 64113 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : For architectural cabinets. 1. Include plans, elevations, sections, and attachment details. 2. Show details. 3. Show locations and sizes of furring, blocking, and hanging strips, including concealed blocking and reinforcement specified in other Sections. 4. Show locations and sizes of cutouts and holes for items installed in architectural cabinets. 5. Show veneer leaves with dimensions, grain direction, exposed face, and identification numbers indicating the flitch and sequence within the flitch for each leaf. 6. Apply AWI Quality Certification Program label to Shop Drawings.
128 | 64116 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, and attachment details. 2. Show large-scale details. 3. Show locations and sizes of furring, blocking, and hanging strips, including concealed blocking and reinforcement specified in other Sections. 4. Show locations and sizes of cutouts and holes for items installed in plastic-laminate architectural cabinets. 5. Apply AWI Quality Certification Program label to Shop Drawings.
137 | 70150.19 | 1.6-B | Product Data | Product Data | Temporary Roofing Submittal : Product data and description of temporary roofing system. 1. If temporary roof remains in place, include surface preparation requirements needed to receive permanent roof, and submita letter from roofing manufacturer stating acceptance of the temporary roof and that its inclusion does not adversely affect the new roofing system's resistance to fire and wind or its FM Approvals rating.
146 | 72726 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : For air-barrier assemblies. 1. Show locations and extent of air-barrier materials, accessories, and assemblies specific to Project conditions. 2. Include details for substrate joints and cracks, counterflashing strips, penetrations, inside and outside corners, terminations, and tie-ins with adjoining construction. 3. Include details of interfaces with other materials that form part of air barrier.
151 | 75423 | 1.5-A | Product Data | Product Data | Product Data : For each type of product. 1. For insulation and roof system component fasteners, include copy of FM Approvals' RoofNav listing.
152 | 75423 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : Include roof plans, sections, details, and attachments to other work, including the following: 1. Layout and thickness of insulation. 2. Base flashings and membrane termination details. 3. Flashing details at penetrations. 4. Tapered insulation layout, thickness, and slopes. 5. Roof plan showing orientation of steel roof deck and orientation of roof membrane, fastening spacings, and patterns for mechanically fastened roofing system. 6. Insulation fastening patterns for corner, perimeter, and field-of-roof locations. 7. Tie-in with adjoining air barrier.
155 | 75423 | 1.5-D | Product Data | Product Data | Wind Uplift Resistance Submittal : For roofing system, indicating compliance with wind uplift performance requirements.
165 | 77200 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : For roof accessories. 1. Include plans, elevations, keyed details, and attachments to other work. Indicate dimensions, loadings, and special conditions. Distinguish between plant- and field- assembled work.
170 | 78100 | 1.5-A | Product Data | Product Data | Product Data : For the following: 1. Sprayed fire-resistive material. 2. Substrate primers. 3. Bonding agent. 4. Metal lath. 5. Reinforcing fabric. 6. Sealer. 7. Topcoat.
171 | 78100 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : Framing plans or schedules, or both, indicating the following: 1. Extent of fire protection for each construction and fire-resistance rating. 2. Applicable fire-resistance design designations ofa qualified testing and inspecting agency acceptable to authorities having jurisdiction. 3. Minimum sprayed fire-resistive material thicknesses needed to achieve required fire- resistance rating of each structural component and assembly. 4. Treatment of sprayed fire-resistive material after application.
192 | 79513.13 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : For each expansion joint cover assembly. 1. Include plans, elevations, sections, details, splices, block-out requirement, attachments to other work, and line diagrams showing entire route of each expansion joint. 2. Where expansion joint cover assemblies change planes, provide isometric or clearly detailed drawing depicting how components interconnect.
195 | 81113 | 1.6-B | Shop Drawings | Shop Drawings | Shop Drawings : Include the following: 1. Elevations of each door type. 2. Details of doors, including vertical- and horizontal-edge details and metal thicknesses. 3. Frame details for each frame type, including dimensioned profiles and metal thicknesses. 4. Locations of reinforcement and preparations for hardware. 5. Details of each different wall opening condition. 6. Details of electrical raceway and preparation for electrified hardware, access control systems, and security systems. 7. Details of anchorages, joints, field splices, and connections. 8. Details of accessories. 9. Details of moldings, removable stops, and glazing.
205 | 83323 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : For each installation and for special components not dimensioned or detailed in manufacturer's product data. 1. Include plans, elevations, sections, and mounting details. 2. Include details of equipment assemblies, and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field connection. 3. Include points of attachment and their corresponding static and dynamic loads imposed on structure. 4. For exterior components, include details of provisions for assembly expansion and contraction and for excluding and draining moisture to the exterior. 5. Show locations of controls, locking devices, and other accessories. 6. Include diagrams for power, signal, and control wiring.
210 | 84313 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : For aluminum-framed storefronts. Include plans, elevations, sections, full-size details, and attachments to other work. 1. Include details of provisions for assembly expansion and contraction and for draining moisture occurring within the assembly to the exterior. 2. Include full-size isometric details of each type of vertical-to-horizontal intersection of aluminum-framed storefronts, showing the following: a. Joinery, including concealed welds. b. Anchorage. c. Expansion provisions. d. Glazing. e. Flashing and drainage. 3. Show connection to and continuity with adjacent thermal, weather, air, and vapor barriers.
224 | 87100 | 1.6-B | Shop Drawings | Shop Drawings | Shop Drawings : For electrified door hardware. 1. Include diagrams for power, signal, and control wiring. 2. Include details of interface of electrified door hardware and building safety and security systems.
251 | 92900 | 1.3-A | Product Data | Product Data | Product Data : For the following: 1. Gypsum wallboard. 2. Gypsum board, Type X. 3. Impact-resistant gypsum board. 4. Mold-resistant gypsum board. 5. Acoustically enhanced gypsum board. 6. Cementitious backer units. 7. Interior trim. 8. Joint treatment materials. 9. Sound-attenuation blankets. 10. Acoustical sealant.
262 | 93013 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : Show locations of each type of tile and tile pattern. Show widths, details, and locations of expansion, contraction, control, and isolation joints in tile substrates and finished tile surfaces.
280 | 96516 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : For each type of resilient sheet flooring. 1. Include sheet flooring layouts, locations of seams, edges, columns, doorways, enclosing partitions, built-in furniture, cabinets, and cutouts. 2. Show details of special patterns.
285 | 96519 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : For each type of resilient floor tile. 1. Include floor tile layouts, edges, columns, doorways, enclosing partitions, built-in furniture, cabinets, and cutouts. 2. Show details of special patterns.
289 | 96566 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : Show installation details and locations of the following: 1. Border tiles. 2. Floor patterns. 3. Layout, colors, widths, and dimensions of game lines and markers. 4. Locations of floor inserts for athletic equipment installed through flooring. 5. Seam locations for sheet flooring.
292 | 96623 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : Include terrazzo installation requirements. Include plans, sections, component details, and relationship to other work. Show layout of the following: 1. Abrasive strips. 2. Stair treads, risers, and landings. 3. Precast terrazzo jointing and edge configurations. 4. Terrazzo patterns.
299 | 96813 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : For carpet tile installation, plans showing the following: 1. Columns, doorways, enclosing walls or partitions, built-in cabinets, and locations where cutouts are required in carpet tiles. 2. Carpet tile type, color, and dye lot. 3. Type of subfloor. 4. Type of installation. 5. Pattern of installation. 6. Pattern type, location, and direction. 7. Pile direction. 8. Type, color, and location of insets and borders. 9. Type, color, and location of edge, transition, and other accessory strips. 10. Transition details to other flooring materials.
307 | 97200 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : Show location and extent of each wall-covering type. Indicate pattern placement, seams, and termination points.
311 | 97713 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : For each stretched-fabric system. 1. Include plans, elevations, sections, and installation and system details. 2. Include details at head, base, joints, and corners; and details at ceiling, floor base, and wall intersections. Indicate frame-edge profile and core materials. 3. Include details at cutouts and penetrations for other work. 4. Include direction of fabric weave and pattern matching. 5. Show sewn-seam locations, types, and methods.
329 | 102113.14 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : For toilet compartments. 1. Include plans, elevations, sections, details, and attachment details. 2. Show locations of cutouts for compartment-mounted toilet accessories. 3. Show locations of reinforcements for compartment-mounted grab bars and locations of blocking for surface-mounted toilet accessories. 4. Show locations of centerlines of toilet fixtures. 5. Show locations of floor drains. 6. Show ceiling grid, ceiling-mounted items, and overhead support or bracing locations.
335 | 102213 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, details, and attachments to other work. 2. Indicate clearances required for operation of doors.
339 | 102219 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : For demountable partitions. 1. Include plans, elevations, sections, and attachment details at floors, columns, permanent partitions, and ceilings; and method of erection and disassembly. 2. Include diagrams for power-, signal-, and control-wiring raceways; and details of access to raceways.
349 | 102233 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : For accordion folding partitions. 1. Include plans, elevations, sections, and attachment details. 2. Indicate storage and operating clearances. 3. Indicate location and installation requirements for hardware and track, blocking, and direction of travel. 4. Indicate facing-material seam locations if any. 5. Include diagrams for power, signal, and control wiring.
356 | 102233 | 1.6-B | Shop Drawings | Shop Drawings | Setting Drawings : For embedded items and cutouts required in other work, including support- beam, mounting-hole template.
363 | 102239.13 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : For operable glass-panel partitions. 1. Include plans, elevations, sections, details, numbered panel installation sequence, and attachments to other work. 2. Indicate stacking and operating clearances. Indicate location and installation requirements for hardware and track, blocking, and direction of travel.
369 | 102239.13 | 1.6-B | Shop Drawings | Shop Drawings | Setting Drawings : For embedded items and cutouts required in other work, including support- beam, mounting-hole template.
375 | 102600 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : For each type of wall and door protection showing locations and extent. 1. Include plans, elevations, sections, and attachment details.
385 | 104413 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : For fire-protection cabinets. 1. Include plans, elevations, sections, details, and attachments to other work. RFI 037 - Samples Required for DFH,
390 | 105123 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : For plastic-laminate-clad wood lockers. 1. Include plans, elevations, sections, and attachment details. 2. Show details full size. 3. Show locations and sizes of furring, blocking, and hanging strips, including concealed blocking and reinforcement specified in other Sections. 4. Show locations and sizes of cutouts and holes for items installed in lockers. 5. Show locker fillers, trim, base, sloping tops, and accessories. 6. Show locker identification system and numbering sequence.
399 | 111316 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, and attachment details. 2. Detail assemblies and indicate dimensions, weights, required clearances, method of field assembly, components, and location and size of anchors and field connection. 3. Include diagrams for power, signal, and control wiring of inflatable blower motor.
401 | 111319 | 1.6-B | Shop Drawings | Shop Drawings | Shop Drawings : For stationary loading dock equipment. 1. Include plans, elevations, sections, and attachment details. 2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of anchors and each field connection. 3. Include diagrams for power, signal, and control wiring.
406 | 115313 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : For laboratory fume hoods. 1. Include plans, elevations, sections, and attachment details. 2. Indicate details for anchoring fume hoods to permanent building construction including locations of blocking and other supports. Include calculations demonstrating that anchorages comply with seismic performance requirements. 3. Indicate locations and types of service fittings together with associated service supply connection required. 4. Indicate duct connections, electrical connections, and locations of access panels. 5. Include roughing-in information for mechanical, plumbing, and electrical connections. 6. Show adjacent walls, doors, windows, other building components, laboratory casework, and other laboratory equipment. Indicate clearances from the above items. 7. Include layout of fume hoods in relation to lighting fixtures and air-conditioning registers and grilles. 8. Include coordinated dimensions for laboratory equipment specified in other Sections.
411 | 118226 | 1.4-B | Shop Drawings | Shop Drawings | Shop Drawings : For each waste compactor and for special components not dimensioned or detailed in manufacturer's product data. 1. Include plans, elevations, sections, and attachment details. 2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection. 3. Dimension chute and diverter locations that interface with waste compactors. 4. Include location and installation details of automatic sprinkler in hopper of each chute- fed compactor. 5. Indicate equipment access points and required space for equipment service and operation. 6. Include setting drawings, templates, and instructions for installing anchor bolts and other anchorages. 7. Include diagrams for power, signal, and control wiring.
415 | 122413 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : Show fabrication and installation details for roller shades, including shadeband materials, their orientation to rollers, and their seam and batten locations. 1. Motor-Operated Shades: Include details of installation and diagrams for power, signal, and control wiring.
423 | 123553.13 | 1.5-B | Shop Drawings | Shop Drawings | Shop Drawings : For laboratory casework. 1. Include plans, elevations, sections, and attachments to other work including blocking and reinforcements required for installation. 2. Indicate types and sizes of casework. 3. Indicate manufacturer's catalog numbers for casework. 4. Show fabrication details, including types and locations of hardware. 5. Indicate locations and types of service fittings. 6. Include details of utility spaces showing supports for conduits and piping. 7. Include details of support framing system. 8. Include details of exposed conduits, if required, for service fittings. 9. Indicate locations of and clearances from adjacent walls, doors, windows, other building components, and laboratory equipment. 10. Include coordinated dimensions for laboratory equipment specified in other Sections.
431 | 123623.13 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : For plastic-laminate-clad countertops. 1. Include plans, sections, details, and attachments to other work. Detail fabrication and installation, including field joints. 2. Show locations and sizes of cutouts and holes for items installed in plastic-laminate-clad countertops. 3. Apply AWI Quality Certification Program label to Shop Drawings.
443 | 123661.16 | 1.3-B | Shop Drawings | Shop Drawings | Shop Drawings : For countertops. Show materials, finishes, edge and backsplash profiles, methods of joining, and cutouts for plumbing fixtures. 1. Show locations and details of joints. 2. Show direction of directional pattern, if any.
450 | 230010 | 1.5 | Product Data | Shop Drawings | General Provide submittals of material or equipment in accordance with the Submittal Requirement Schedule at the end of this specification section. Some sections have very specific submittal requirements, not indicated in this section, and therefore are indicated in that specific specification section. A submittal is required if an X is indicated for that column and item. Acceptable Manufacturers Subject to compliance with the requirements of the individual specification sections, provide materials and equipment from the indicated manufacturers only. Submittals of material or equipment manufactured by other than those indicated will be returned. If no manufacturers are indicated, then any product or material that complies with the specification and for the intended application is acceptable. If manufacturers are indicated, the first manufacturer in section list, or scheduled manufacturer or datasheet indicated manufacturer is the "basis of design", and all other indicated manufacturers are acceptable alternative manufacturers, as long as they also comply with the specification. It should be noted that there may be differences in dimension or installation requirements between the basis of design and others indicated and that additional work that may be required by other trades needs to be coordinated with the other trades and provided at no extra cost to the owner. Submittal Procedures Coordination: Coordinate preparation and processing of submittals with performance of construction activities. Transmit each submittal sufficiently in advance of performance of related construction activities to avoid delay. Coordinate each submittal with fabrication, purchasing, testing, delivery, other submittals and related activities that requires sequential activity. Coordinate transmittal of different types of submittals for related elements of the work so processing will not be delayed by the need to review submittals concurrently for coordination. The Owner or Owner's Representative reserves the right to withhold action ona submittal requiring coordination with other submittals until related submittals are received. Processing: Allow sufficient review time so that installation will not be delayed asa result of the time required to process submittals, including time for resubmittals. Allow ten working days for initial review. Allow additional time if processing must be delayed to permit coordination with subsequent submittals. The Owner or Owner's Representative will promptly advise the Contractor whena submittal being processed must be delayed for coordination. If an intermediate submittal is necessary, process the same as the initial submittal. Allow ten working days for reprocessing each submittal. No extension of contract time will be authorized because of failure to transmit submittals to the Owner or Owner's Representative sufficiently in advance of the work to permit processing. Submittal Preparation: Placea permanent label or title block on each submittal for identification. Indicate the name of the entity that prepared each submittal on the label or title block. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Contractor's review and approval markings and the action taken. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Owner's or Owner's Representative review and approval markings and the action taken. Include the following information on the label or title block for processing and recording action taken. Project name Date Name and address of Owner Name and address of Engineer Name and address of Contractor Name and address of subcontractor Name and address of supplier Name of manufacturer Number and title of appropriate Specification Section Drawing number and detail references, as appropriate Unique Submittal Number for each package Submittal Transmittal: Package each submittal appropriately for transmittal and handling. Transmittal shall list specification section for each item submitted. Transmit each submittal from Contractor to Owner or Owner's Representative usinga transmittal form. Submittals received from sources other than the Contractor will be returned without action. Submittals: Submit one (1) electronic copy of each required submittal ina single combined PDF format with all individual specification sections separated individually. The Engineer will mark and return one (1) electronic copy in PDF format with action taken and corrections or modifications required. Owner will retain one (1) electronic copy of returned document. Retain copy of each for O&M manuals or Enhanced Turn Over Packages (ETOPs). Schedules: Project schedules indicating proposed work phases and sequences. Include in schedule asa minimum, approvals, equipment release, delivery, fabrication, equipment setting, startup, punch, and cleanup. Submittal Schedule Prepare and submita complete schedule of submittals. Coordinate submittal schedule with the construction schedule. Prepare the schedule in chronological order. Provide the following information: Scheduled date for submittal Related Section number Submittal category Name of subcontractor Description of the part of the work covered Anticipated date for Engineer's final release or approval Schedule Updating: Revise the schedule after each meeting or activity, where revisions have been recognized or made. Issue the updated schedule to all parties involved. 1.5.1. Review Action The Contractor is responsible for all data and information on submittals, including quantities, sizes, dimensions, and compliance with the Drawings and Specifications. Checking by the Owner or Owner's Representative is only for general conformance with the design concept of the project and general compliance with the information given in the Contract Documents. Any action shown is subject to the requirements of the Drawings and Specifications. Contractor is responsible for dimensions and quantities, which shall be confirmed at the job site, and fabrication process and techniques of construction. On the submittal, record relevant information and requests for data. Record deviations from Contract Document requirements, including minor variations and limitations. Include Contractor's certification that information complies with Contract Document requirements. Except for submittals for record, information for similar purposes, where action and return is required or requested, the Owner will check each submittal, mark to indicate action taken, and return promptly. Compliance with specified characteristics is the Contractor's responsibility. 1.5.2. Shop Drawings Submit information, drawn to accurate scale. Highlight, encircle, or otherwise indicate deviations from the Contract Documents. Do not reproduce Contract Documents or copy standard information as the basis of Shop Drawings. Standard information prepared without specific reference to the Project is not considered Shop Drawings. Shop Drawings include fabrication and installation drawings, setting diagrams, schedules, patterns, templates and similar drawings, and directions for installation of anchorages. Include asa minimum the following information on drawings or diagrams: Dimensions Identification of products and materials included Compliance with specified standards Notation of coordination requirements Notation of dimensions established by field measurement Clearances for access and service Sheet Size: Except for templates, patterns and similar full-size drawings, submit Shop Drawings in PDF format at least 8" x 11", but no larger than 30" x 42". Initial Submittal: (Where Contractor desires product specific information or preliminary review prior to processing of final submittal.) Submit an electronic copy of prints in PDF format for the Owner's review. Final Submittal: Submit electronic copy of all prints. An electronic set of prints will be retained and maintained asa Record Document. The Owner's representative has the right to mark up the final submittal. Do not use Shop Drawings without an appropriate final stamp indicating action taken in connection with construction. 1.5.3. Coordination Drawings or 3D (BIM) Model: Mechanical, Electrical, Plumbing and Fire Protection Contract Drawings or 3D (BIM) model are diagrammatic. They are not intended to be precise; they are not intended to specify or to show every offset, fitting, and component. The purpose of the drawings or 3D (BIM) model is to indicatea systems concept, the main components of the systems, and the approximate geometrical relationships. Information and components shown on diagrams, but not shown on plans, and vice versa, shall apply or be provided as if expressly required on both. The contractor shall provide coordination drawings or 3D (BIM) model; detailing major elements, components, and systems of mechanical equipment and materials in relationship with other systems, installations, and building components. Indicate locations where space is limited for installation and access and where sequencing and coordination of installations are of importance to the efficient flow of the Work. Refer to the Project's BIM execution plan. Drawings or 3D (BIM) model shall include but shall not be limited to the following: Clearances for installing and maintaining installation. Clearances for servicing and maintaining equipment, including tube removal, filter removal, valves and space for equipment disassembly required for periodic maintenance. Equipment connections and support details. Exterior wall and roof penetrations. Fire-rated wall and floor penetrations. Sizes and locations of required concrete pads and bases. Valve stem movement. Plumbing systems, piping and equipment. HVAC
451 | 230038 | 1.2 | Calculations | Shop Drawings | Product Data: Submit manufacturer's technical data describing environmental chambers. The Data Sheet attached with this document shall be completed by all manufacturers submitting bids. This sheet shall be reviewed by the Owner/Designer and shall be used for final selection of manufacturer. All details must be provided as requested. All details denoted with VS (Vendor Supplied) must be provided as requested. Upon award, submit shop drawings showing layout, elevations, typical sections and details. Show plans, elevations and sections at not less than 1/4 inch scale; show details at not less than 1-1/2 inch scale. All utility requirements (power, water, drain, etc.) shall be provided. Wiring diagrams, piping schematics, component cut sheets and specifications shall also be provided after award and prior to startup. General: Show total layout of Controlled Environment Room(s) with relationship to adjacent building construction and equipment, fabrication and installation details, wall panel and roof panel data, door information, windows, materials, gages, fasteners, flashing, trim pieces and closures. Calculations: Supporting equipment selection. Indicate design loads added for door openings, air changes, direct supply air, lighting, personnel, process equipment, environmental room equipment and product load. Controls: Submit complete single-line diagrams, schematic diagrams, wiring diagrams, software descriptions, and all other details required to demonstrate that system has been coordinated and will properly function asa system. Provide outline dimensions, mounting details, weights, power requirements, console/cabinet/panel arrangements, system functional descriptions, Input/Output (I/O) point summary and I/O signal conditioning requirements. Refrigerants: Refrigerant Charge in pounds of refrigerant per ton of cooling capacity. Refrigerant Type. Equipment Type. Closeout Submittals: Operation and Maintenance Manuals: Include startup, operation and maintenance instructions, parts listing with sources indicated; recommended spare parts inventory listing, emergency instructions and similar information. Control systems: Include complete single-line diagrams, schematic diagrams, wiring diagrams, outline dimensions, mounting details, weights, power requirements, console/cabinet/panel arrangements, system functional descriptions, Input/Output (I/O) point summary and I/O signal conditioning requirements. Wiring diagrams to clearly show connetion points for remote monitoring signals. Testing Reports: Refrigerant Testing and Charging reports, Temperature Mapping, etc. Keys: Three (3) sets of marked and identified keys to operate all key operated functions, including control panel door
452 | 230038 | 1.2 | Shop Drawings | Shop Drawings | Product Data: Submit manufacturer's technical data describing environmental chambers. The Data Sheet attached with this document shall be completed by all manufacturers submitting bids. This sheet shall be reviewed by the Owner/Designer and shall be used for final selection of manufacturer. All details must be provided as requested. All details denoted with VS (Vendor Supplied) must be provided as requested. Upon award, submit shop drawings showing layout, elevations, typical sections and details. Show plans, elevations and sections at not less than 1/4 inch scale; show details at not less than 1-1/2 inch scale. All utility requirements (power, water, drain, etc.) shall be provided. Wiring diagrams, piping schematics, component cut sheets and specifications shall also be provided after award and prior to startup. General: Show total layout of Controlled Environment Room(s) with relationship to adjacent building construction and equipment, fabrication and installation details, wall panel and roof panel data, door information, windows, materials, gages, fasteners, flashing, trim pieces and closures. Calculations: Supporting equipment selection. Indicate design loads added for door openings, air changes, direct supply air, lighting, personnel, process equipment, environmental room equipment and product load. Controls: Submit complete single-line diagrams, schematic diagrams, wiring diagrams, software descriptions, and all other details required to demonstrate that system has been coordinated and will properly function asa system. Provide outline dimensions, mounting details, weights, power requirements, console/cabinet/panel arrangements, system functional descriptions, Input/Output (I/O) point summary and I/O signal conditioning requirements. Refrigerants: Refrigerant Charge in pounds of refrigerant per ton of cooling capacity. Refrigerant Type. Equipment Type. Closeout Submittals: Operation and Maintenance Manuals: Include startup, operation and maintenance instructions, parts listing with sources indicated; recommended spare parts inventory listing, emergency instructions and similar information. Control systems: Include complete single-line diagrams, schematic diagrams, wiring diagrams, outline dimensions, mounting details, weights, power requirements, console/cabinet/panel arrangements, system functional descriptions, Input/Output (I/O) point summary and I/O signal conditioning requirements. Wiring diagrams to clearly show connetion points for remote monitoring signals. Testing Reports: Refrigerant Testing and Charging reports, Temperature Mapping, etc. Keys: Three (3) sets of marked and identified keys to operate all key operated functions, including control panel door
458 | 230575 | 1.1 | Calculations | Certificates | Certificates: Submit certificates of materials compliance with specified ASTM, UL and ASHRAE requirements, NFPA 54 National Fuel Gas Code, and NFPA 31 Installation of Oil-Burning Equipment Certificates: Submit Welders' Qualification Certificates. Certificates: Submit complete engineering report certifying that stacks meet the design wind and seismic loads.
459 | 230835 | 1.4 | Shop Drawings | Shop Drawings | Submit shop drawings for all coils in compliance with Section 230010 requirements. Submittals shall include all performance data noted in schedules.
460 | 230856 | 1.4 | Shop Drawings | Shop Drawings | General: Refer to specifications 230010 and 230050 for additional requirements. Product data shall include dimensions, weights, capacities, certifications, component performance, electrical characteristics, casing construction details, wiring interconnections, gauges and material finishes. The submittal shall provide all technical information relevant to the product being provided, including but not limited to, all the information shown in the attached schedules and drawings(s). It is the responsibility of the supplier to highlight any variances the equipment has with the requirements of this specification whether or not pre-approval has been obtained. Information shall be provided in the same measurement units as indicated in the schedules and drawings(s). The submittal(s) shall provide independent fan curves for operating/design conditions [not fan tables], with specified operating/design points clearly plotted. The submittal(s) shall provide coil selection worksheets, clearly showing proper consideration for altitude, air density, glycol corrections and indicate coil tube fin and casing construction. The submittal(s) shall provide filter information, including: initial (clean) APD, final (dirty) APD, dust spot efficiency, final dust holding capacity, filter media description, filter frame details, and filter removal details. The manufacturer shall submit sound power levels for both air handling unit inlet, outlet and radiated at rated capacity. The manufacturer shall submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring. The manufacturer shall submit the manufacturers recommended installation instructions. Provide drawings of unit arrangement with dimensions for system and sections including utility connections. Omission of any of the above information will cause shop drawings to be immediately returned without review.
462 | 230856 | 1.4 | Product Data | Shop Drawings | General: Refer to specifications 230010 and 230050 for additional requirements. Product data shall include dimensions, weights, capacities, certifications, component performance, electrical characteristics, casing construction details, wiring interconnections, gauges and material finishes. The submittal shall provide all technical information relevant to the product being provided, including but not limited to, all the information shown in the attached schedules and drawings(s). It is the responsibility of the supplier to highlight any variances the equipment has with the requirements of this specification whether or not pre-approval has been obtained. Information shall be provided in the same measurement units as indicated in the schedules and drawings(s). The submittal(s) shall provide independent fan curves for operating/design conditions [not fan tables], with specified operating/design points clearly plotted. The submittal(s) shall provide coil selection worksheets, clearly showing proper consideration for altitude, air density, glycol corrections and indicate coil tube fin and casing construction. The submittal(s) shall provide filter information, including: initial (clean) APD, final (dirty) APD, dust spot efficiency, final dust holding capacity, filter media description, filter frame details, and filter removal details. The manufacturer shall submit sound power levels for both air handling unit inlet, outlet and radiated at rated capacity. The manufacturer shall submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring. The manufacturer shall submit the manufacturers recommended installation instructions. Provide drawings of unit arrangement with dimensions for system and sections including utility connections. Omission of any of the above information will cause shop drawings to be immediately returned without review.
468 | 230910 | 1.4 | Shop Drawings | Samples | PART 2. - PRODUCTS.......................................................................................................................................... 2
469 | 230910 | 1.4 | Shop Drawings | Shop Drawings | Product Data: For each type of product indicated. Shop Drawings: Indicate installation details in ductwork and other construction. Provide wiring diagrams.
470 | 230932 | 1.4 | Product Data | Samples | PART 2. - PRODUCTS.......................................................................................................................................... 2
471 | 230932 | 1.4 | Product Data | Product Data | Product Data: For each type of product indicated, include the following: Indicate materials of construction, finish, and mounting details; and performance data including throw and drop, static-pressure drop, accessories and noise ratings. It is the responsibility of any manufacturer providing submittals to verify in advance their performance criteria is similar to Basis of Design (BOD) manufacturer in the following criteria. General compatibility- style, construction, ceiling or wall integration, fastening, color and accessories. Performance: NC level shall be equal to or less than BOD Static and total pressure shall be equal to or less than BOD Isothermal throw data at 150/100/50 fpm shall be within plus or minus 5% of the BOD values for standard products. Air devices for labs and critical spaces shall be shown with cooling temperature differentials of 5/10/15 degrees and throws of 100/75/50/30 fpm. Data shall be presented by computerized selection software. Catalog charts and graphs are not acceptable unless the tabular data is rated within 10% of the BOD performance selected. Manufacturers not complying with all portions of requirements will be rejected and not subject to further review by the design professional.
472 | 260524 | 1.5 | Shop Drawings | Shop Drawings | Product Data: For each type of product. Include rated capacities, operating characteristics, furnished specialties, and accessories for each type of product indicated. Schedule heating capacity, length of cable, spacing, and electrical power requirement for each electric heating cable required. Shop Drawings: For each heating cable, include plans, sections, details, and attachments to other work. Include wiring diagrams for heating cable power, signal, and control wiring. Include panel information and details, wiring diagrams, load information, installation details. Operation and Maintenance Data: Provide heating cable and control system operation and maintenance manuals.
473 | 260534 | 1.4 | Shop Drawings | Shop Drawings | Product Data: For each type of product including but not limited to materials, finishes, separators and miscellaneous components. Shop Drawings: For floor boxes, custom enclosures and cabinets. Include plans, elevations, sections, and attachment details. Coordination Drawings: Dimensioned floor box, and other in-slab box(es), location drawings. Included dimensioned plans using architectural floor plans, furniture system(s) floor plans, and structural floor plans. Indicate location of known underground utilities or structures. Dimensioned handhole, and other in-grade box(es), location drawings. Included dimensioned plans using architectural site plans, civil site plans, and structural site plans. Indicate location of known underground utilities or structures. Product Certificates: For concrete and steel used in precast concrete handholes, as required by ASTM C 858 and comply with BGE requirements.
477 | 260536 | 1.1 | Shop Drawings | Shop Drawings | Shop Drawings: Layout floor plans and elevations showing cable tray system. Designate components and accessories including clamps, brackets, hanger rods, splice plate connectors, expansion joint assemblies, straight lengths, and fittings. Show accurately scaled components and spatial relationships to adjacent equipment. Show tray types, dimensions, and finishes. Factory Test Reports: Certified copies of factory test reports performed in conformance with NEMA Standard VE 1 on cable trays of types and size specified for this project.
479 | 262416 | 1.5 | Shop Drawings | Product Data | Product Data: For each type of panelboard, switching and overcurrent protective device, surge protection device, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: For each panelboard and related equipment, include: Dimensioned plans, elevations, sections, and details. Show tabulations of installed equipment features, and ratings. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. Detail bus configuration, current, and voltage ratings. Qualification Data: For qualified testing agency. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Panelboard Schedules: For installation in panelboards. Operation and Maintenance Data: For panelboards and components to include in emergency, operation, and maintenance manuals.
483 | 262416 | 1.5 | Maintenance Data | Product Data | Product Data: For each type of panelboard, switching and overcurrent protective device, surge protection device, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: For each panelboard and related equipment, include: Dimensioned plans, elevations, sections, and details. Show tabulations of installed equipment features, and ratings. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. Detail bus configuration, current, and voltage ratings. Qualification Data: For qualified testing agency. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Panelboard Schedules: For installation in panelboards. Operation and Maintenance Data: For panelboards and components to include in emergency, operation, and maintenance manuals.
484 | 262816 | 1.5 | Shop Drawings | Product Data | Product Data: For each type of enclosure, switching and overcurrent protective device, surge protection device, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: For each enclosure and related equipment, include: Dimensioned plans, elevations, sections, and details. Show tabulations of installed equipment features, and ratings. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. Detail bus configuration, current, and voltage ratings. Qualification Data: For qualified testing agency. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For equipment and components to include in emergency, operation, and maintenance manuals.
487 | 262816 | 1.5 | Maintenance Data | Product Data | Product Data: For each type of enclosure, switching and overcurrent protective device, surge protection device, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: For each enclosure and related equipment, include: Dimensioned plans, elevations, sections, and details. Show tabulations of installed equipment features, and ratings. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. Detail bus configuration, current, and voltage ratings. Qualification Data: For qualified testing agency. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For equipment and components to include in emergency, operation, and maintenance manuals.
488 | 262913 | 1.4 | Shop Drawings | Product Data | Product Data: For each type of enclosed controller, enclosure, switching and overcurrent protection, surge protection device, accessory, and component indicated. Include dimensions and manufacturers technical data on features, performance, electrical characteristics, performance, ratings, and finishes. Shop Drawings: For each enclosed controller. Include dimensioned plans, elevations, sections, details, and required clearances and service spaces around controller enclosures. Show tabulations of the following: Each installed unit's type and details. Factory-installed devices. Nameplate legends. Short-circuit current rating of integrated unit. Listed and labeled for integrated short-circuit current (withstand) rating of OCPDs in combination controllers by an NRTL acceptable to authorities having jurisdiction. Features, characteristics, ratings, and factory settings of individual OCPDs in combination controllers. Wiring Diagrams: For power, signal, and control wiring. Operation and Maintenance Data: For enclosed controllers to include in emergency, operation, and maintenance manuals. In addition to items specified in include the following: Routine maintenance requirements for enclosed controllers and installed components. Manufacturer's written instructions for testing and adjusting circuit breaker and MCP trip settings. Manufacturer's written instructions for setting field-adjustable overload relays. Manufacturer's written instructions for testing, adjusting, and reprogramming reduced-voltage solid- state controllers. Load-Current and List of Settings of Adjustable Overload Relays: Compile after motors have been installed, and arrange to demonstrate that switch settings for motor running overload protection suit actual motors to be protected. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Load-Current and List of Settings of Adjustable Overload Relays: Compile after motors have been installed, and arrange to demonstrate that switch settings for motor running overload protection suit actual motors to be protected. Load-Current and Overload-Relay Heater List: Compile after motors installation and arrange to demonstrate that selection of heaters suits actual motor nameplate full-load currents. Operation and Maintenance Data: For equipment and components to include in emergency, operation, and maintenance manuals. Routine maintenance requirements for enclosed controllers and installed components. Manufacturer's written instructions for testing and adjusting circuit breaker and MCP trip settings. Manufacturer's written instructions for setting field-adjustable overload relays. Manufacturer's written instructions for testing, adjusting, and reprogramming reduced-voltage solid- state controllers.
489 | 262913 | 1.4 | Maintenance Data | Product Data | Product Data: For each type of enclosed controller, enclosure, switching and overcurrent protection, surge protection device, accessory, and component indicated. Include dimensions and manufacturers technical data on features, performance, electrical characteristics, performance, ratings, and finishes. Shop Drawings: For each enclosed controller. Include dimensioned plans, elevations, sections, details, and required clearances and service spaces around controller enclosures. Show tabulations of the following: Each installed unit's type and details. Factory-installed devices. Nameplate legends. Short-circuit current rating of integrated unit. Listed and labeled for integrated short-circuit current (withstand) rating of OCPDs in combination controllers by an NRTL acceptable to authorities having jurisdiction. Features, characteristics, ratings, and factory settings of individual OCPDs in combination controllers. Wiring Diagrams: For power, signal, and control wiring. Operation and Maintenance Data: For enclosed controllers to include in emergency, operation, and maintenance manuals. In addition to items specified in include the following: Routine maintenance requirements for enclosed controllers and installed components. Manufacturer's written instructions for testing and adjusting circuit breaker and MCP trip settings. Manufacturer's written instructions for setting field-adjustable overload relays. Manufacturer's written instructions for testing, adjusting, and reprogramming reduced-voltage solid- state controllers. Load-Current and List of Settings of Adjustable Overload Relays: Compile after motors have been installed, and arrange to demonstrate that switch settings for motor running overload protection suit actual motors to be protected. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Load-Current and List of Settings of Adjustable Overload Relays: Compile after motors have been installed, and arrange to demonstrate that switch settings for motor running overload protection suit actual motors to be protected. Load-Current and Overload-Relay Heater List: Compile after motors installation and arrange to demonstrate that selection of heaters suits actual motor nameplate full-load currents. Operation and Maintenance Data: For equipment and components to include in emergency, operation, and maintenance manuals. Routine maintenance requirements for enclosed controllers and installed components. Manufacturer's written instructions for testing and adjusting circuit breaker and MCP trip settings. Manufacturer's written instructions for setting field-adjustable overload relays. Manufacturer's written instructions for testing, adjusting, and reprogramming reduced-voltage solid- state controllers.
493 | 263323 | 1.5 | Shop Drawings | Product Data | Product Data: For each type of central battery equipment unit, include performance, electrical ratings, product data sheets, operating characteristics, battery warranty, input and output circuit breakers, integrated distribution panels, shipping and operating weights, self-diagnostic features, shipping splits, and furnished options, specialties, and accessories. Shop Drawings: For each type and rating of central battery equipment unit, include: Plans, elevations, sections, and mounting details. Details of equipment assemblies: indicate dimensions, weights, loads, required clearances, ventilation requirements, method of field assembly, components, and locations and size of each field connection. System one-line diagram, internal and interconnecting wiring; and diagrams for power, signal, and control wiring. Short-circuit current rating of inverter and overcurrent protective devices. Elevation, details, and legends of control and indication displays. Source quality control reports Informational Submittals: Coordination Drawings: Floor plans, drawn to scale, showing dimensioned layout, required working clearances, and required area above and around central battery equipment. Show central battery equipment layout and relationships between electrical components and adjacent structural and mechanical elements. Show support locations, type of support, and weight on each support. Indicate field measurements. Qualification Data: for installer and testing agency. Product Certificates: For each type of central battery equipment. Field-Quality Control Reports: Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For central battery inverter and components to include in emergency, operation, and maintenance manuals. Operation and Maintenance Data: For central battery equipment to include in emergency, operation, and maintenance manuals. o Manufacturer's written instructions for testing central battery equipment. o Manufacturer's written instructions for testing, adjusting, and reprogramming microprocessor control modules. o Manufacturer's written instructions for selecting and setting field-adjustable controls and status and alarm points o Manufacturers listed gallons of electrolyte per battery cell
497 | 263323 | 1.5 | Maintenance Data | Product Data | Product Data: For each type of central battery equipment unit, include performance, electrical ratings, product data sheets, operating characteristics, battery warranty, input and output circuit breakers, integrated distribution panels, shipping and operating weights, self-diagnostic features, shipping splits, and furnished options, specialties, and accessories. Shop Drawings: For each type and rating of central battery equipment unit, include: Plans, elevations, sections, and mounting details. Details of equipment assemblies: indicate dimensions, weights, loads, required clearances, ventilation requirements, method of field assembly, components, and locations and size of each field connection. System one-line diagram, internal and interconnecting wiring; and diagrams for power, signal, and control wiring. Short-circuit current rating of inverter and overcurrent protective devices. Elevation, details, and legends of control and indication displays. Source quality control reports Informational Submittals: Coordination Drawings: Floor plans, drawn to scale, showing dimensioned layout, required working clearances, and required area above and around central battery equipment. Show central battery equipment layout and relationships between electrical components and adjacent structural and mechanical elements. Show support locations, type of support, and weight on each support. Indicate field measurements. Qualification Data: for installer and testing agency. Product Certificates: For each type of central battery equipment. Field-Quality Control Reports: Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For central battery inverter and components to include in emergency, operation, and maintenance manuals. Operation and Maintenance Data: For central battery equipment to include in emergency, operation, and maintenance manuals. o Manufacturer's written instructions for testing central battery equipment. o Manufacturer's written instructions for testing, adjusting, and reprogramming microprocessor control modules. o Manufacturer's written instructions for selecting and setting field-adjustable controls and status and alarm points o Manufacturers listed gallons of electrolyte per battery cell
498 | 263600 | 1.5 | Shop Drawings | Product Data | Product Data: For each type of transfer switch, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, weights, and finishes. Shop Drawings: For each transfer switch, include: Dimensioned plans, elevations, sections, details, and required clearances and service spaces around transfer switch enclosures. Show connections between transfer switch, power sources, and load. Show interconnection wiring between transfer switches, annunciators, control panels, generators, and building monitoring systems. Qualification Data: For qualified testing agency. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For each type of transfer switch and components include operation and maintenance manual. In addition to items specified in Division 01 Section Operation and Maintenance Data, include the following: Features and operating sequences, both automatic and manual. List of all factory settings of relays; provide relay-setting and calibration instructions, including software, where applicable.
501 | 263600 | 1.5 | Maintenance Data | Product Data | Product Data: For each type of transfer switch, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, weights, and finishes. Shop Drawings: For each transfer switch, include: Dimensioned plans, elevations, sections, details, and required clearances and service spaces around transfer switch enclosures. Show connections between transfer switch, power sources, and load. Show interconnection wiring between transfer switches, annunciators, control panels, generators, and building monitoring systems. Qualification Data: For qualified testing agency. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For each type of transfer switch and components include operation and maintenance manual. In addition to items specified in Division 01 Section Operation and Maintenance Data, include the following: Features and operating sequences, both automatic and manual. List of all factory settings of relays; provide relay-setting and calibration instructions, including software, where applicable.
503 | 264113 | 1.3 | Shop Drawings | Shop Drawings | Product Data: For each type of product indicated, for example: grounding down conductors, through roof/through wall assemblies, roof conductors, air terminals, accessories, and components required. Include dimensions, weights, and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: Showing the type, size, and locations of grounding down conductors, through roof/through wall assemblies, roof conductors, and air terminals, indicating the extent of the system layout designed specifically for the building(s) or structures included in the contract drawings along with details of the products to be used in the installation. Shop drawings shall include indications for use of raceway, data on how concealment requirements will be met, and calculations required by NFPA 780 for bonding of grounded and isolated metal bodies. Shop drawings shall be submitted to the Architect and the Engineer for approval prior to commencement of the installation. If any departures from the contract drawings or submittal drawings covered below are deemed necessary by the Contractor, details of such departures and reasons therefore shall be submitted as soon as practical to the Architect/Engineer for approval. Certification and Qualification Data: For Lightning Protection Institute (LPI) Certified designer and installer. Upon request, submit evidence of such qualifications to the Engineer.