## Sheet 1
S. No. | Spec # | Spec Name | Para | Sub Section Heading | Submittal Type | Submittal Description | Target Date | Subcontractor
155 | 024119 | SELECTIVE DEMOLITION | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For refrigerant recovery technician.
156 | 024119 | SELECTIVE DEMOLITION | 1.5-B | INFORMATIONAL SUBMITTALS | Engineering Survey | Engineering Survey : Submit engineering survey of condition of building.
157 | 024119 | SELECTIVE DEMOLITION | 1.5-C | INFORMATIONAL SUBMITTALS | Measurements | Proposed Protection Measures : Submit report, including Drawings, that indicates the measures proposed for protecting individuals and property, for dust control and for noise control. Indicate proposed locations and construction of barriers.
158 | 024119 | SELECTIVE DEMOLITION | 1.5-D | INFORMATIONAL SUBMITTALS | Schedules | Schedule of Selective Demolition Activities : Indicate the following: 1. Detailed sequence of selective demolition and removal work, with starting and ending dates for each activity. Ensure Owner's on-site operations are uninterrupted. 2. Interruption of utility services. Indicate how long utility services will be interrupted. 3. Coordination for shutoff, capping, and continuation of utility services. 4. Use of elevator and stairs. 5. Coordination of Owner's continuing occupancy of portions of existing building and of Owner's partial occupancy of completed Work.
159 | 024119 | SELECTIVE DEMOLITION | 1.5-E | INFORMATIONAL SUBMITTALS | Photos | Predemolition Photographs or Video : Show existing conditions of adjoining construction, including finish surfaces that might be misconstrued as damage caused by demolition operations.
160 | 024119 | SELECTIVE DEMOLITION | 1.5-F | INFORMATIONAL SUBMITTALS | Statement Of Refrigerant Recovery | Statement of Refrigerant Recovery : Signed by refrigerant recovery technician responsible for recovering refrigerant, stating that all refrigerant that was present was recovered and that recovery was performed according to EPA regulations. Include name and address of technician and date refrigerant was recovered.
161 | 024119 | SELECTIVE DEMOLITION | 1.5-G | INFORMATIONAL SUBMITTALS | Warranty | Warranties : Documentation indicating that existing warranties are still in effect after completion of selective demolition.
162 | 024119 | SELECTIVE DEMOLITION | 1.6-A | CLOSEOUT SUBMITTALS | Inventory | Inventory : Submita list of items that have been removed and salvaged.
163 | 031000 | CONCRETE FORMING AND ACCESSORIES | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Review the following: a. Special inspection and testing and inspecting agency procedures for field quality control. b. Construction, movement, contraction, and isolation joints c. Forms and form-removal limitations. d. Shoring and reshoring procedures. e. Anchor rod and anchorage device installation tolerances.
164 | 031000 | CONCRETE FORMING AND ACCESSORIES | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each of the following: 1. Exposed surface form-facing material. 2. Concealed surface form-facing material. 3. Pan-type forms. 4. Waterstops.
165 | 031000 | CONCRETE FORMING AND ACCESSORIES | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Prepared by, and signed and sealed by, a qualified professional engineer responsible for their preparation, detailing fabrication, assembly, and support of forms. 1. Indicate dimension and locations of construction and movement joints required to construct the structure in accordance with ACI 301. a. Location of construction joints is subject to approval of the Architect. 2. Indicate location of waterstops.
166 | 031000 | CONCRETE FORMING AND ACCESSORIES | 1.5-C | ACTION SUBMITTALS | Samples | Samples : - 1. For waterstops.
167 | 031000 | CONCRETE FORMING AND ACCESSORIES | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For testing and inspection agency.
168 | 031000 | CONCRETE FORMING AND ACCESSORIES | 1.6-B | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
169 | 031000 | CONCRETE FORMING AND ACCESSORIES | 1.6-C | INFORMATIONAL SUBMITTALS | Meeting Minutes | Minutes of preinstallation conference.
171 | 031000 | CONCRETE FORMING AND ACCESSORIES | 1.7-B | QUALITY ASSURANCE | Mockups | Mockups : Formed surfaces to demonstrate typical joints, surface finish, texture, tolerances, and standard of workmanship. 1. Build panel approximately 100 sq. ft. in the location indicated or, if not indicated, as directed by Architect. 2. Subject to compliance with requirements, approved mockups may become part of the completed Work.
175 | 032000 | CONCRETE REINFORCING | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Review the following: a. Special inspection and testing and inspecting agency procedures for field quality control. b. Construction contraction and isolation joints. c. Steel-reinforcement installation.
176 | 032000 | CONCRETE REINFORCING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For the following: 1. Each type of steel reinforcement. 2. Epoxy repair coating. 3. Zinc repair material. 4. Bar supports.
177 | 032000 | CONCRETE REINFORCING | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Comply with ACI SP-066: 1. Include placing drawings that detail fabrication, bending, and placement. 2. Include bar sizes, lengths, materials, grades, bar schedules, stirrup spacing, bent bar diagrams, bar arrangement, location of splices, lengths of lap splices, details of mechanical splice couplers, details of welding splices, tie spacing, hoop spacing, and supports for concrete reinforcement.
178 | 032000 | CONCRETE REINFORCING | 1.4-C | ACTION SUBMITTALS | Construction Joint Layout | Construction Joint Layout : Indicate proposed construction joints required to build the structure. 1. Location of construction joints is subject to approval of the Architect.
179 | 032000 | CONCRETE REINFORCING | 1.4-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For structural thermal break insulated connection system, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
180 | 032000 | CONCRETE REINFORCING | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Statements : For [delegated-design engineer] [testing and inspection agency].
181 | 032000 | CONCRETE REINFORCING | 1.5-B | INFORMATIONAL SUBMITTALS | Delegated-Design Submittal | Delegated-Design Engineer Qualifications : Include the following: 1. Experience providing delegated-design engineering services of the type indicated. 2. Documentation that delegated-design engineer is licensed in the state in which Project is located.
182 | 032000 | CONCRETE REINFORCING | 1.5-C | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates. 1. Reinforcement to Be Welded: Welding procedure specification in accordance with AWS D1.4/D1.4M
183 | 032000 | CONCRETE REINFORCING | 1.5-D | INFORMATIONAL SUBMITTALS | Test Reports | Material Test Reports : For the following, froma qualified testing agency: 1. Steel Reinforcement: a. For reinforcement to be welded, mill test analysis for chemical composition and carbon equivalent of the steel in accordance with ASTM A706/A706M.
184 | 032000 | CONCRETE REINFORCING | 1.5-E | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
185 | 032000 | CONCRETE REINFORCING | 1.5-F | INFORMATIONAL SUBMITTALS | Meeting Minutes | Minutes of preinstallation conference.
188 | 032000 | CONCRETE REINFORCING | 1.6-C | QUALITY ASSURANCE | Mockups | Mockups : Reinforcing for cast-concrete formed surfaces, to demonstrate tolerances and standard of workmanship. 1. Build panel approximately 100 sq. ft. for formed surface in the location indicated on Drawings or, if not indicated, as directed by Architect. 2. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
212 | 033000 | CAST-IN-PLACE CONCRETE | 1.11-A | WARRANTY | Manufacturers Warranty | Manufacturer's Warranty : Manufacturer agrees to furnish replacement sheet vapor retarder/termite barrier material and accessories for sheet vapor retarder/ termite barrier and accessories that do not comply with requirements or that fail to resist penetration by termites within specified warranty period. 1. Warranty Period: 10 years from date of Substantial Completion.
193 | 033000 | CAST-IN-PLACE CONCRETE | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Require representatives of each entity directly concerned with cast-in-place concrete to attend, including the following: a. Contractor's superintendent. b. Independent testing agency responsible for concrete design mixtures. c. Ready-mix concrete manufacturer. d. Concrete Subcontractor. e. Special concrete finish Subcontractor. 2. Review the following: a. Special inspection and testing and inspecting agency procedures for field quality control. b. Construction joints, control joints, isolation joints, and joint-filler strips. c. Semirigid joint fillers. d. Vapor-retarder installation. e. Anchor rod and anchorage device installation tolerances. f. Cold and hot weather concreting procedures. g. Concrete finishes and finishing. h. Curing procedures. i. Forms and form-removal limitations. j. Shoring and reshoring procedures. k. Methods for achieving specified floor and slab flatness and levelness. l. Floor and slab flatness and levelness measurements. m. Concrete repair procedures. n. Concrete protection. o. Initial curing and field curing of field test cylinders (ASTM C31/C31M.) p. Protection of field cured field test cylinders.
194 | 033000 | CAST-IN-PLACE CONCRETE | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each of the following. 1. Portland cement. 2. Fly ash. 3. Slag cement. 4. Blended hydraulic cement. 5. Silica fume. 6. Performance-based hydraulic cement 7. Aggregates. 8. Admixtures: a. Include limitations of use, including restrictions on cementitious materials, supplementary cementitious materials, air entrainment, aggregates, temperature at time of concrete placement, relative humidity at time of concrete placement, curing conditions, and use of other admixtures. 9. Color pigments. 10. Fiber reinforcement. 11. Vapor retarders. 12. Floor and slab treatments. 13. Liquid floor treatments. 14. Curing materials. a. Include documentation from color pigment manufacturer, indicating that proposed methods of curing are recommended by color pigment manufacturer. 15. Joint fillers. 16. Repair materials.
195 | 033000 | CAST-IN-PLACE CONCRETE | 1.5-B | ACTION SUBMITTALS | Mix Design | Design Mixtures : For each concrete mixture, include the following: 1. Mixture identification. 2. Minimum 28-day compressive strength. 3. Durability exposure class. 4. Maximum w/cm. 5. Calculated equilibrium unit weight, for lightweight concrete. 6. Slump limit. 7. Air content. 8. Nominal maximum aggregate size. 9. Steel-fiber reinforcement content. 10. Synthetic micro-fiber content. 11. Indicate amounts of mixing water to be withheld for later addition at Project site if permitted. 12. Include manufacturer's certification that permeability-reducing admixture is compatible with mix design. 13. Include certification that dosage rate for permeability-reducing admixture matches dosage rate used in performance compliance test. 14. Intended placement method. 15. Submit alternate design mixtures when characteristics of materials, Project conditions, weather, test results, or other circumstances warrant adjustments.
196 | 033000 | CAST-IN-PLACE CONCRETE | 1.5-C | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Construction Joint Layout: Indicate proposed construction joints required to construct the structure. a. Location of construction joints is subject to approval of the Architect.
197 | 033000 | CAST-IN-PLACE CONCRETE | 1.5-D | ACTION SUBMITTALS | Samples | Samples : For manufacturer's standard colors for color pigment, vapor retarder.
198 | 033000 | CAST-IN-PLACE CONCRETE | 1.5-E | ACTION SUBMITTALS | Schedules | Concrete Schedule : For each location of each Class of concrete indicated in "Concrete Mixtures" Article, including the following: 1. Concrete Class designation. 2. Location within Project. 3. Exposure Class designation. 4. Formed Surface Finish designation and final finish. 5. Final finish for floors. 6. Curing process. 7. Floor treatment if any.
199 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For the following: 1. Installer: Include copies of applicable ACI certificates. 2. Ready-mixed concrete manufacturer. 3. Testing agency: Include copies of applicable ACI certificates.
200 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each of the following, signed by manufacturers: 1. Cementitious materials. 2. Admixtures. 3. Fiber reinforcement. 4. Curing compounds. 5. Floor and slab treatments. 6. Bonding agents. 7. Adhesives. 8. Vapor retarders. 9. Semirigid joint filler. 10. Joint-filler strips. 11. Repair materials.
201 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-C | INFORMATIONAL SUBMITTALS | Test Reports | Material Test Reports : For the following, froma qualified testing agency: 1. Portland cement. 2. Fly ash. 3. Slag cement. 4. Blended hydraulic cement. 5. Silica fume. 6. Performance-based hydraulic cement. 7. Aggregates. 8. Admixtures: a. Permeability-Reducing Admixture: Include independent test reports, indicating compliance with specified requirements, including dosage rate used in test.
202 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-D | INFORMATIONAL SUBMITTALS | Measurements | Floor surface flatness and levelness measurements report, indicating compliance with specified tolerances.
203 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-E | INFORMATIONAL SUBMITTALS | Reports | Research Reports : - 1. For concrete admixtures in accordance with ICC's Acceptance Criteria AC198. 2. For sheet vapor retarder/termite barrier, showing compliance with ICC AC380.
204 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-F | INFORMATIONAL SUBMITTALS | Test Reports | Preconstruction Test Reports : For each mix design.
205 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-G | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
206 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-H | INFORMATIONAL SUBMITTALS | Meeting Minutes | Minutes of preinstallation conference.
211 | 033000 | CAST-IN-PLACE CONCRETE | 1.7-E | QUALITY ASSURANCE | Mockups | Mockups : Cast concrete slab-on-ground panels to demonstrate typical joints, surface finish, texture, tolerances, floor treatments, and standard of workmanship. 1. Slab-On-Ground: Build panel approximately 15 feet by 15 feet in the location indicated or, if not indicated, as directed by Architect. a. Divide panel into four equal panels to demonstrate saw joint cutting. 2. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
219 | 051200 | STRUCTURAL STEEL FRAMING | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
220 | 051200 | STRUCTURAL STEEL FRAMING | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : - 1. Structural-steel materials. 2. High-strength, bolt-nut-washer assemblies. 3. Shear stud connectors. 4. Anchor rods. 5. Threaded rods. 6. Forged-steel hardware. 7. Slide bearings. 8. Prefabricated building columns. 9. Shop primer. 10. Galvanized-steel primer. 11. Etching cleaner. 12. Galvanized repair paint. 13. Shrinkage-resistant grout.
221 | 051200 | STRUCTURAL STEEL FRAMING | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Show fabrication of structural-steel components. 1. Include details of cuts, connections, splices, camber, holes, and other pertinent data. 2. Include embedment Drawings. 3. Indicate welds by standard AWS symbols, distinguishing between shop and field welds, and show size, length, and type of each weld. Show backing bars that are to be removed and supplemental fillet welds where backing bars are to remain. 4. Indicate type, size, and length of bolts, distinguishing between shop and field bolts. Identify pretensioned and slip-critical, high-strength bolted connections. 5. Identify members and connections of the seismic-load-resisting system. 6. Indicate locations and dimensions of protected zones. 7. Identify demand-critical welds. 8. Identify members not to be shop primed.
222 | 051200 | STRUCTURAL STEEL FRAMING | 1.5-C | ACTION SUBMITTALS | Qualification Data | Welding Procedure Specifications (WPSs) and Procedure Qualification Records (PQRs) : Provide in accordance with AWS D1.1/D1.1M for each welded joint whether prequalified or qualified by testing, including the following: 1. Power source (constant current or constant voltage). 2. Electrode manufacturer and trade name, for demand-critical welds.
223 | 051200 | STRUCTURAL STEEL FRAMING | 1.5-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated Design Submittal : For structural-steel connections indicated on Drawings to comply with design loads, include analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
224 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer, fabricator, shop-painting applicators, professional engineer, testing agency.
225 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
226 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-C | INFORMATIONAL SUBMITTALS | Certificates | Paint Compatibility Certificates : From manufacturers of topcoats applied over shop primers, certifying that shop primers are compatible with topcoats.
227 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-D | INFORMATIONAL SUBMITTALS | Test Reports | Mill test reports for structural-steel materials, including chemical and physical properties.
228 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-E | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For the following: 1. Bolts, nuts, and washers, including mechanical properties and chemical analysis. 2. Direct-tension indicators. 3. Tension-control, high-strength, bolt-nut-washer assemblies. 4. Shear stud connectors.
229 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-F | INFORMATIONAL SUBMITTALS | General | Survey of existing conditions.
230 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-G | INFORMATIONAL SUBMITTALS | Reports | Source quality-control reports.
231 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-H | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
239 | 053100 | STEEL DECKING | 1.2-A | ACTION SUBMITTALS | Product Data | Product Data : - 1. Roof deck. 2. Acoustical roof deck. 3. Composite floor deck. 4. Electrified cellular floor deck. 5. Noncomposite form deck. 6. Noncomposite vented form deck.
240 | 053100 | STEEL DECKING | 1.2-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include layout and types of deck panels, anchorage details, reinforcing channels, pans, cut deck openings, special jointing, accessories, and attachments to other construction.
241 | 053100 | STEEL DECKING | 1.3-A | INFORMATIONAL SUBMITTALS | Certificates | Certificates : - 1. Welding certificates. 2. Product Certificates: For each type of steel deck.
242 | 053100 | STEEL DECKING | 1.3-B | INFORMATIONAL SUBMITTALS | Reports | Test and Evaluation Reports : - 1. Product Test Reports: For tests performed bya qualified testing agency, indicating that each of the following complies with requirements: a. Power-actuated mechanical fasteners. b. Acoustical roof deck. 2. Research Reports: For steel deck, from ICC-ES showing compliance with the building code.
243 | 053100 | STEEL DECKING | 1.3-C.1 | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
244 | 053100 | STEEL DECKING | 1.3-D | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Statements : For welding personnel and testing agency.
251 | 054000 | COLD-FORMED METAL FRAMING | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
252 | 054000 | COLD-FORMED METAL FRAMING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For the following: 1. Cold-formed steel framing materials. 2. Load-bearing wall framing. 3. Exterior non-load-bearing wall framing. 4. Interior non-load-bearing wall framing. 5. Vertical deflection clips. 6. Single deflection track. 7. Double deflection track. 8. Drift clips. 9. Floor joist framing. 10. Roof-rafter framing. 11. Ceiling joist framing. 12. Soffit framing. 13. Post-installed anchors. 14. Power-actuated anchors. 15. Sill sealer gasket. 16. Sill sealer gasket/termite barrier.
253 | 054000 | COLD-FORMED METAL FRAMING | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include layout, spacings, sizes, thicknesses, and types of cold-formed steel framing; fabrication; and fastening and anchorage details, including mechanical fasteners. 2. Indicate reinforcing channels, opening framing, supplemental framing, strapping, bracing, bridging, splices, accessories, connection details, and attachment to adjoining work.
254 | 054000 | COLD-FORMED METAL FRAMING | 1.4-C | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For cold-formed steel framing.
255 | 054000 | COLD-FORMED METAL FRAMING | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For testing agency.
256 | 054000 | COLD-FORMED METAL FRAMING | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
257 | 054000 | COLD-FORMED METAL FRAMING | 1.5-C | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of code-compliance certification for studs and tracks.
258 | 054000 | COLD-FORMED METAL FRAMING | 1.5-D | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each listed product, for tests performed by manufacturer and witnessed bya qualified testing agency. 1. Steel sheet. 2. Expansion anchors. 3. Power-actuated anchors. 4. Mechanical fasteners. 5. Vertical deflection clips. 6. Horizontal drift deflection clips 7. Miscellaneous structural clips and accessories.
259 | 054000 | COLD-FORMED METAL FRAMING | 1.5-E | INFORMATIONAL SUBMITTALS | Reports | Research Reports : - 1. For nonstandard cold-formed steel framing post-installed anchors and power-actuated fasteners, from ICC-ES or other qualified testing agency acceptable to authorities having jurisdiction. 2. For sill sealer gasket/termite barrier, showing compliance with ICC-ES AC380.
270 | 055000 | METAL FABRICATIONS | 1.4-A | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Show fabrication and installation details. Include plans, elevations, sections, and details of metal fabrications and their connections. Show anchorage and accessory items. Provide Shop Drawings for the following: 1. Steel framing and supports for overhead doors and grilles. 2. Steel framing and supports for countertops. 3. Steel framing and supports for mechanical and electrical equipment. 4. Steel framing and supports for overhead piping. 5. Stainless steel toe kicks and similar closures around equipment. 6. Steel framing and supports for applications where framing and supports are not specified in other Sections. 7. Metal ladders. 8. Miscellaneous steel trim including steel angle corner guards, steel edgings, and loading-dock edge angles. 9. Metal bollards. 10. Abrasive metal nosings, treads, and thresholds.
273 | 055050 | STAINLESS STEEL FABRICATIONS | 1.3-A | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Show fabrication and installation details. Include plans, elevations, sections, and details of stainless-steel fabrications and their connections and clearances around equipment. Show anchorage and accessory items including, but not limited to, manufacturer type of fasteners, manufacturer of adhesives, type, material and dimensions of each anchorage and accessory item. Provide Shop Drawings for all items to be provided under this Section.
274 | 055050 | STAINLESS STEEL FABRICATIONS | 1.3-B | ACTION SUBMITTALS | Samples | Samples for Verification : - 1. Finishes: For each type of exposed finish required, prepared on samples of not less than 3 by 5 inches. a. Provide samples for No. 4 stainless-steel finishes for Owners Representative and Architects approval.
275 | 055050 | STAINLESS STEEL FABRICATIONS | 1.3-C | ACTION SUBMITTALS | Samples | Fabrication Sample : Of each welded joint of assemblies, made from 6-inch lengths of components and showing details of inside corners, outside corners, flush welds, and special conditions.
277 | 055113 | METAL PAN STAIRS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For metal pan stairs and the following: 1. Abrasive nosings. 2. Shop primer products. 3. Nonslip-aggregate concrete finish. 4. Handrail wall brackets. 5. Grout.
278 | 055113 | METAL PAN STAIRS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, details, and attachments to other work. 2. Indicate sizes of metal sections, thickness of metals, profiles, holes, and field joints. 3. Include plan at each level. 4. Indicate locations of anchors, weld plates, and blocking for attachment of wall-mounted handrails.
279 | 055113 | METAL PAN STAIRS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type and finish of nosing.
280 | 055113 | METAL PAN STAIRS | 1.5-A | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
281 | 055113 | METAL PAN STAIRS | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Paint Compatibility Certificates : From manufacturers of topcoats applied over shop primers, certifying that shop primers are compatible with topcoats.
284 | 055213 | PIPE AND TUBE RAILINGS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : - 1. Manufacturer's product lines of mechanically connected railings. 2. Fasteners. 3. Post-installed anchors. 4. Handrail brackets. 5. Shop primer. 6. Intermediate coats and topcoats. 7. Bituminous paint. 8. Non-shrink, nonmetallic grout. 9. Anchoring cement. 10. Metal finishes. 11. Paint products.
285 | 055213 | PIPE AND TUBE RAILINGS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include plans, elevations, sections, details, and attachments to other work.
286 | 055213 | PIPE AND TUBE RAILINGS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed finish required. 1. Sections of each distinctly different linear railing member, including handrails, top rails, posts, and balusters, including finish. 2. Fittings and brackets. 3. Assembled Sample of railing system, made from full-size components, including top rail, post, handrail, and infill. Sample need not be full height. a. Show method of connecting and finishing members at intersections.
296 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 1.10-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of roofing system that fail in materials or workmanship within specified warranty period. 1. Special warranty includes roofing membrane, base flashings, and other components of roofing system. 2. Warranty Period: 10 years from date of Substantial Completion.
297 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 1.10-B | WARRANTY | Special Warranty | Special Project Warranty : Submit roofing Installer's warranty, on warranty form at end of this Section, signed by Installer, covering the Work of this Section, including all components of roofing system, such as roofing membrane, base flashing for the following warranty period: 1. Warranty Period: Two years from date of Substantial Completion.
288 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Roofing Conference : Conduct conference at Project site. 1. Meet with Owner, Construction Manager, Architect, Owner's insurer if applicable, testing and inspecting agency representative, roofing Installer, roofing system manufacturer's representative, deck Installer, air barrier Installer, and installers whose work interfaces with or affects roofing, including installers of roof accessories and roof-mounted equipment. 2. Review methods and procedures related to roofing installation, including manufacturer's written instructions. 3. Review and finalize construction schedule, and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays. 4. Examine deck substrate conditions and finishes for compliance with requirements, including flatness and fastening. 5. Review structural loading limitations of roof deck during and after roofing. 6. Review base flashings, special roofing details, roof drainage, roof penetrations, equipment curbs, and condition of other construction that affects roofing. 7. Review governing regulations and requirements for insurance and certificates if applicable. 8. Review temporary protection requirements for roofing system during and after installation. 9. Review roof observation and repair procedures after roofing installation.
289 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. For insulation and roof system component fasteners, include copy of FM Approvals' RoofNav listing.
290 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include plans, sections, details, and attachments to other work, including the following: 1. Base flashings and roofing terminations. 2. Flashing details at penetrations. 3. Crickets, saddles, and tapered edge strips, including slopes.
291 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Verification : For the following products: 1. Cap Sheet: Samples of manufacturer's standard colors for selection by Architect. 2. Flashing Sheet: Samples of manufacturer's standard colors for selection by Architect.
292 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 1.6-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For roofing system to include in maintenance manuals.
293 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 1.6-B | CLOSEOUT SUBMITTALS | Warranty | Certified statement from existing roof membrane manufacturer, stating that existing roof warranty has not been affected by Work performed under this Section.
301 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 3.7-A | ROOFING INSTALLER'S WARRANTY | Warranty | WHEREAS _______________________________ of ___________________________, herein called the "Roofing Installer," has performed roofing and associated work ("work") on the following project: 1. Owner: Takeda 2. Address: 4501 Colorado Ave., Los Angeles, CA 90039 3. Building Name/Type: San Fernando Warehouse 4. Address: 4501 Colorado Ave., Los Angeles, CA 90039. 5. Area of Work: roof top equipment platform: structural, piping, and ductwork penetrations 6. Acceptance Date: _________________. 7. Warranty Period: 2 years 8. Expiration Date: __________________.
302 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 3.7-B | ROOFING INSTALLER'S WARRANTY | Warranty | AND WHEREAS Roofing Installer has contracted (either directly with Owner or indirectly asa subcontractor) to warrant said work against leaks and faulty or defective materials and workmanship for designated Warranty Period,
303 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 3.7-C | ROOFING INSTALLER'S WARRANTY | Warranty | NOW THEREFORE Roofing Installer hereby warrants, subject to terms and conditions herein set forth, that during Warranty Period Roofing Installer will, at Roofing Installer's own cost and expense, make or cause to be made such repairs to or replacements of said work as are necessary to correct faulty and defective work and as are necessary to maintain said work ina watertight condition.
304 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 3.7-D | ROOFING INSTALLER'S WARRANTY | Warranty | This Warranty is made subject to the following terms and conditions : - 1. Specifically excluded from this Warranty are damages to work and other parts of the building, and to building contents, caused by: a. lightning. b. peak gust wind speed exceeding 110 mph c. fire. d. failure of roofing system substrate, including cracking, settlement, excessive deflection, deterioration, and decomposition. e. faulty construction of parapet walls, copings, chimneys, skylights, vents, equipment supports, and other edge conditions and penetrations of the work. f. vapor condensation on bottom of roofing; and g. activity on roofing by others, including construction contractors, maintenance personnel, other persons, and animals, whether authorized or unauthorized by Owner. 2. When work has been damaged by any of foregoing causes, Warranty shall be null and void until such damage has been repaired by Roofing Installer and until cost and expense thereof have been paid by Owner or by another responsible party so designated. 3. Roofing Installer is responsible for damage to work covered by this Warranty but is not liable for consequential damages to building or building contents resulting from leaks or faults or defects of work. 4. During Warranty Period, if Owner allows alteration of work by anyone other than Roofing Installer, including cutting, patching, and maintenance in connection with penetrations, attachment of other work, and positioning of anything on roof, this Warranty shall become null and void on date of said alterations, but only to the extent said alterations affect work covered by this Warranty. If Owner engages Roofing Installer to perform said alterations, Warranty shall not become null and void unless Roofing Installer, before starting said work, shall have notified Owner in writing, showing reasonable cause for claim, that said alterations would likely damage or deteriorate work, thereby reasonably justifyinga limitation or termination of this Warranty. 5. During Warranty Period, if original use of roof is changed and it becomes used for, but was not originally specified for, a promenade, work deck, spray-cooled surface, flooded basin, or other use or service more severe than originally specified, this Warranty shall become null and void on date of said change, but only to the extent said change affects work covered by this Warranty. 6. Owner shall promptly notify Roofing Installer of observed, known, or suspected leaks, defects, or deterioration and shall afford reasonable opportunity for Roofing Installer to inspect work and to examine evidence of such leaks, defects, or deterioration. 7. This Warranty is recognized to be the only warranty of Roofing Installer on said work and shall not operate to restrict or cut off Owner from other remedies and resources lawfully available to Owner in cases of roofing failure. Specifically, this Warranty shall not operate to relieve Roofing Installer of responsibility for performance of original work according to requirements of the Contract Documents, regardless of whether Contract wasa contract directly with Owner ora subcontract with Owner's General Contractor.
305 | 075113.01 | BUILT-UP ASPHALT ROOFING MODIFICATIONS | 3.7-E | ROOFING INSTALLER'S WARRANTY | Warranty | IN WITNESS THEREOF, this instrument has been duly executed this ___________ day of ___________________, ________________. 1. Authorized Signature: _______________________________________. 2. Name: ______________________________________. 3. Title: _______________________________________.
306 | 076200 | SHEET METAL FLASHING AND TRIM | 1.4-A | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For sheet metal flashing and trim. 1. Include plans, elevations, sections, and attachment details. 2. Detail fabrication and installation layouts, expansion-joint locations, and keyed details. Distinguish between shop- and field-assembled work. 3. Include identification of material, thickness, weight, and finish for each item and location in Project. 4. Include details for forming, including profiles, shapes, seams, and dimensions. 5. Include details for joining, supporting, and securing, including layout and spacing of fasteners, cleats, clips, and other attachments. Include pattern of seams. 6. Include details of termination points and assemblies. 7. Include details of expansion joints and expansion-joint covers, including showing direction of expansion and contraction from fixed points. 8. Include details of roof-penetration flashing. 9. Include details of edge conditions, including eaves, ridges, valleys, rakes, crickets, and counter flashings as applicable. 10. Include details of special conditions. 11. Include details of connections to adjoining work. 12. Detail formed flashing and trim at scale of not less than 1-1/2 inches per 12 inches.
307 | 076200 | SHEET METAL FLASHING AND TRIM | 1.4-B | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed finish. 1. Sheet Metal Flashing: 12 inches long by actual width of unit, including finished seam and in required profile. Include fasteners, cleats, clips, closures, and other attachments. 2. Trim, Metal Closures, Expansion Joints, Joint Intersections, and Miscellaneous Fabrications: 12 inches long and in required profile. Include fasteners and other exposed accessories.
309 | 076200 | SHEET METAL FLASHING AND TRIM | 1.7-A | WARRANTY | Special Warranty | Special Warranty on Finishes : Manufacturer agrees to repair finish or replace sheet metal flashing and trim that shows evidence of deterioration of factory-applied finishes within specified warranty period. 1. Exposed Panel Finish: Deterioration includes, but is not limited to, the following: a. Color fading more than 5 Hunter units when tested according to ASTM D 2244. b. Chalking in excess ofa No. 8 rating when tested according to ASTM D 4214. c. Cracking, checking, peeling, or failure of paint to adhere to bare metal. 2. Finish Warranty Period: 20 years from date of Substantial Completion.
310 | 079200 | JOINT SEALANTS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each joint-sealant product.
311 | 079200 | JOINT SEALANTS | 1.3-B | ACTION SUBMITTALS | Samples | Samples for Initial Selection : Manufacturer's color charts consisting of strips of cured sealants showing the full range of colors available for each product exposed to view.
312 | 079200 | JOINT SEALANTS | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each kind and color of joint sealant required, provide Samples with joint sealants in 1/2-inch-wide joints formed between two 6-inch-long strips of material matching the appearance of exposed surfaces adjacent to joint sealants.
313 | 079200 | JOINT SEALANTS | 1.3-D | ACTION SUBMITTALS | Schedules | Joint-Sealant Schedule : Include the following information: 1. Joint-sealant application, joint location, and designation. 2. Joint-sealant manufacturer and product name. 3. Joint-sealant formulation. 4. Joint-sealant color.
314 | 079200 | JOINT SEALANTS | 1.6-A | WARRANTY | Special Warranty | Special Installer's Warranty : Installer agrees to repair or replace joint sealants that do not comply with performance and other requirements specified in this Section within specified warranty period. 1. Warranty Period: Two years from date of Substantial Completion.
315 | 079200 | JOINT SEALANTS | 1.6-B | WARRANTY | Manufacturers Warranty | Special Manufacturer's Warranty : Manufacturer agrees to furnish joint sealants to repair or replace those joint sealants that do not comply with performance and other requirements specified in this Section within specified warranty period. 1. Warranty Period: Five years from date of Substantial Completion.
316 | 079200 | JOINT SEALANTS | 1.6-C | WARRANTY | Special Warranty | Special warranties specified in this article exclude deterioration or failure of joint sealants from the following: 1. Movement of the structure caused by stresses on the sealant exceeding sealant manufacturer's written specifications for sealant elongation and compression. 2. Disintegration of joint substrates from causes exceeding design specifications. 3. Mechanical damage caused by individuals, tools, or other outside agents. 4. Changes in sealant appearance caused by accumulation of dirt or other atmospheric contaminants.
319 | 079200 | JOINT SEALANTS | 3.7-A | JOINT-SEALANT SCHEDULE | Schedules | Joint-Sealant Application : Exterior joints in vertical surfaces and horizontal nontraffic surfaces <JS- #>. 1. Joint Locations: a. Construction joints in cast-in-place concrete. b. Control and expansion joints in unit masonry. c. Joints in exterior insulation and finish systems. d. Joints between different materials listed above. e. Perimeter joints between materials listed above and frames of doors, windows, and louvers. f. Other joints as indicated on Drawings. 2. Joint Sealant: Silicone, nonstaining, S, NS, 50, NT. 3. Joint-Sealant Color: As selected by Owners Representative from manufacturer's full range of colors. Joint-Sealant Application : Interior joints in vertical surfaces and horizontal nontraffic surfaces. 1. Joint Locations: a. Control and expansion joints on exposed interior surfaces of exterior walls. b. Tile control and expansion joints. c. Vertical joints on exposed surfaces of walls. d. Other joints as indicated on Drawings. 2. Joint Sealant: Urethane, S, NS, 25, NT. 3. Joint-Sealant Color: As selected by Owners Representative from manufacturer's full range of colors. Joint-Sealant Application : Interior joints in vertical surfaces and horizontal nontraffic surfaces not subject to significant movement. 1. Joint Locations: a. Control joints on exposed interior surfaces of exterior walls. b. Perimeter joints between interior wall surfaces and frames of interior doors windows and elevator entrances. c. Other joints as indicated on Drawings. 2. Joint Sealant: Acrylic latex. 3. Joint-Sealant Color: As selected by Owners Representative from manufacturer's full range of colors. Joint-Sealant Application : Concealed mastics. 1. Joint Locations: a. Aluminum thresholds. b. Sill plates. c. Other joints as indicated on Drawings. 2. Joint Sealant: Butyl-rubber based. 3. Joint-Sealant Color: As selected by Owners Representative from manufacturer's full range of colors.
320 | 079219 | ACOUSTICAL JOINT SEALANTS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each acoustical joint sealant.
321 | 079219 | ACOUSTICAL JOINT SEALANTS | 1.3-B | ACTION SUBMITTALS | Samples | Samples for Verification : For each kind and color of acoustical joint sealant required, provide Samples with joint sealants in 1/2-inch-wide joints formed between two 6-inch-long strips of material matching the appearance of exposed surfaces adjacent to joint sealants.
322 | 079219 | ACOUSTICAL JOINT SEALANTS | 1.3-C | ACTION SUBMITTALS | Schedules | Acoustical-Joint-Sealant Schedule : Include the following information: 1. Joint-sealant application, joint location, and designation. 2. Joint-sealant manufacturer and product name. 3. Joint-sealant formulation. 4. Joint-sealant color.
323 | 079219 | ACOUSTICAL JOINT SEALANTS | 1.4-A | WARRANTY | Special Warranty | Special Installer's Warranty : Installer agrees to repair or replace acoustical joint sealants that do not comply with performance and other requirements specified in this Section within specified warranty period. 1. Warranty Period: 5 years from date of Substantial Completion.
324 | 079219 | ACOUSTICAL JOINT SEALANTS | 1.4-B | WARRANTY | Manufacturers Warranty | Special Manufacturer's Warranty : Manufacturer agrees to furnish acoustical joint sealants to repair or replace those joint sealants that do not comply with performance and other requirements specified in this Section within specified warranty period. 1. Warranty Period: Two years from date of Substantial Completion.
325 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for expansion joint cover assemblies.
326 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For each expansion joint cover assembly. 1. Include plans, elevations, sections, details, splices, block-out requirement, attachments to other work, and line diagrams showing entire route of each expansion joint. 2. Where expansion joint cover assemblies change planes, provide isometric or clearly detailed drawing depicting how components interconnect.
327 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.3-C | ACTION SUBMITTALS | Samples | Samples : For each expansion joint cover assembly and for each color and texture specified, full width by 6 inches long in size.
328 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.3-D | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of exposed finish. 1. Include manufacturer's color charts showing the full range of colors and finishes available for each exposed metal and elastomeric-seal material.
329 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.3-E | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of expansion joint cover assembly, full width by 6 inches long in size.
330 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.3-F | ACTION SUBMITTALS | Schedules | Expansion Joint Cover Assembly Schedule : Prepared by or under the supervision of the supplier. Include the following information in tabular form: 1. Manufacturer and model number for each expansion joint cover assembly. 2. Expansion joint cover assembly location cross-referenced to Drawings. 3. Nominal, minimum, and maximum joint width. 4. Movement direction. 5. Materials, colors, and finishes. 6. Product options. 7. Fire-resistance ratings.
331 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.4-A | QUALITY ASSURANCE | Mockups | Mockups : Build mockups to demonstrate aesthetic effects and to set quality standards for materials and execution. 1. Build mockup of typical expansion joint cover assembly as shown on Drawings. 2. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing. 3. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
332 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, core descriptions, fire-resistance ratings, and finishes.
333 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include the following: 1. Elevations of each door type. 2. Details of doors, including vertical- and horizontal-edge details and metal thicknesses. 3. Frame details for each frame type, including dimensioned profiles and metal thicknesses. 4. Locations of reinforcement and preparations for hardware. 5. Details of each different wall opening condition. 6. Details of anchorages, joints, field splices, and connections. 7. Details of accessories. 8. Details of moldings, removable stops, and glazing. 9. Details of conduit and preparations for power, signal, and control systems.
334 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Verification : - 1. For each type of exposed finish required, prepared on Samples of not less than 8 by 10 inches.
335 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.5-D | ACTION SUBMITTALS | Schedules | Schedule : Providea schedule of hollow-metal work prepared by or under the supervision of supplier, using same reference numbers for details and openings as those on Drawings. Coordinate with final Door Hardware Schedule.
336 | 081119 | STAINLESS-STEEL DOORS AND FRAMES | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site
337 | 081119 | STAINLESS-STEEL DOORS AND FRAMES | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, core descriptions, fire-resistance ratings and finishes.
338 | 081119 | STAINLESS-STEEL DOORS AND FRAMES | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include the following: 1. Elevations of each door type. 2. Details of doors, including vertical and horizontal edge details and metal thicknesses. 3. Frame details for each frame type, including dimensioned profiles and metal thicknesses. 4. Locations of reinforcement and preparations for hardware. 5. Details of each different wall opening condition. 6. Details of electrical raceway and preparation for electrified hardware, access control systems, and security systems. 7. Details of anchorages, joints, field splices, and connections. 8. Details of accessories. 9. Details of moldings, removable stops, and glazing.
339 | 081119 | STAINLESS-STEEL DOORS AND FRAMES | 1.5-C | ACTION SUBMITTALS | Samples | Samples : - 1. Finishes: For each type of exposed finish required, prepared on Samples of not less than 3 by 5 inches. 2. Doors: Show vertical-edge, top, and bottom construction; core construction; glazing, and hinge and other applied hardware reinforcement. 3. Frames: Show profile, corner joint, floor and wall anchors, and silencers. Include separate section showing fixed hollow-metal panels and glazing if applicable.
340 | 081119 | STAINLESS-STEEL DOORS AND FRAMES | 1.5-D | ACTION SUBMITTALS | Product Schedule | Product Schedule : For stainless steel doors and frames, prepared by or under the supervision of supplier, using same reference numbers for details and openings as those on Drawings. Coordinate with final door hardware schedule.
341 | 081119 | STAINLESS-STEEL DOORS AND FRAMES | 1.6-A | CLOSEOUT SUBMITTALS | As-Builts | Record Documents : For fire-rated doors, list of door numbers and applicable room name and number to which door accesses.
342 | 083113 | ACCESS DOORS AND FRAMES | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, fire ratings, material descriptions, dimensions of individual components and profiles, and finishes.
343 | 083113 | ACCESS DOORS AND FRAMES | 1.4-B | ACTION SUBMITTALS | Samples | Samples : For each type of access door and frame and for each finish specified, complete assembly minimum 6 by 6 inches in size.
344 | 083113 | ACCESS DOORS AND FRAMES | 1.4-C | ACTION SUBMITTALS | Product Schedule | Product Schedule : For access doors and frames.
345 | 083113 | ACCESS DOORS AND FRAMES | 1.4-C-1 | ACTION SUBMITTALS | Shop Drawings | Shop Drawings: a. Include details of each frame type, elevation of panel, anchorage and accessory items. b. Schedule showing each type of access panel and frame, locations, sizes, latching or locking provisions, and other data pertinent to installation. c. Indicate installation procedures and accessories required fora complete installation.
346 | 083123 | FLOOR DOORS | 1.2-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, materials, individual components and profiles, and finishes.
347 | 083123 | FLOOR DOORS | 1.2-B | ACTION SUBMITTALS | Product Schedule | Product Schedule : For floor doors (list). 1. Type A.
348 | 083123 | FLOOR DOORS | 1.3-A | CLOSEOUT SUBMITTALS | As-Builts | Record Documents : For fire-rated floor doors, list of applicable room name and number in which floor door is located.
350 | 083329 | HIGH PERFORMANCE ROLL UP DOORS A | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type and size of high-performance roll-up door and accessory. Include the following: 1. Construction details, material descriptions, dimensions of individual components, and finishes. 2. Operating characteristics, electrical characteristics, and furnished accessories.
351 | 083329 | HIGH PERFORMANCE ROLL UP DOORS A | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For each installation and for special components not dimensioned or detailed in manufacturer's product data. Include plans, elevations, sections, details, and attachments to other work. 1. Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection. 2. Wiring Diagrams: For power, signal, and control wiring. 3. Confirm door actuation on Shop Drawings.
352 | 083329 | HIGH PERFORMANCE ROLL UP DOORS A | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : Manufacturer's finish charts showing full range of colors and textures available for units with factory-applied finishes. Include similar Samples of accessories involving color selection.
353 | 083329 | HIGH PERFORMANCE ROLL UP DOORS A | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For high-performance roll-up doors to include in maintenance manuals.
358 | 083329 | HIGH PERFORMANCE ROLL UP DOORS A | 1.7-A | WARRANTIES | Warranty | One-year limited warranty on all components.
359 | 083329 | HIGH PERFORMANCE ROLL UP DOORS A | 3.5-A | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain overhead roll-up doors.
360 | 085119 | STAINLESS STEEL WINDOWS | 1.2-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, fabrication methods, dimensions of individual components and profiles, hardware, finishes, and operating instructions.
361 | 085119 | STAINLESS STEEL WINDOWS | 1.2-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Plans, elevations, sections, and details. 2. Detail attachments to other work, and between units, if any. 3. Mullion details, including reinforcement and stiffeners. 4. Glazing details. 5. Accessories.
362 | 085119 | STAINLESS STEEL WINDOWS | 1.2-C | ACTION SUBMITTALS | Samples | Samples for Verification : Actual sample of finished products for each type of cold-rolled stainless steel window including weather stripping, glazing bead, and hardware. 1. Size: fit to field verified rough openings.
363 | 085119 | STAINLESS STEEL WINDOWS | 1.2-D | ACTION SUBMITTALS | Sample Warranty | Sample warranties.
364 | 085119 | STAINLESS STEEL WINDOWS | 1.3-A | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For cold-rolled stainless steel windows.
365 | 085119 | STAINLESS STEEL WINDOWS | 1.3-B | CLOSEOUT SUBMITTALS | Warranty | Warranty Documentation : - 1. Manufacturers' special warranties. 2. Installer's special warranties.
367 | 085119 | STAINLESS STEEL WINDOWS | 1.5-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer and Installer agree to repair or replace components of cold-rolled stainless steel windows that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Structural failures. 2. Warranty Period: Two years from date of Substantial Completion.
368 | 087100 | DOOR HARDWARE | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product indicated. Include construction and installation details, material descriptions, dimensions of individual components and profiles, and finishes.
369 | 087100 | DOOR HARDWARE | 1.3-B.1 | ACTION SUBMITTALS | Schedules | Door Hardware Schedule: Prepared by or under the supervision of Installer, detailing fabrication and assembly of door hardware, as well as installation procedures and diagrams. Coordinate final door hardware schedule with doors, frames, and related work to ensure proper size, thickness, hand, function, and finish of door hardware. a. Submittal Sequence: Submit door hardware schedule concurrent with submissions of Product Data, Samples, and Shop Drawings. Coordinate submission of door hardware schedule with scheduling requirements of other work to facilitate the fabrication of other work that is critical in Project construction schedule. b. Format: Comply with scheduling sequence and vertical format in DHI's "Sequence and Format for the Hardware Schedule." Double space entries, and number and date each page. c. Format: Use same scheduling sequence and format and use same door numbers as in the Contract Documents. d. Content: Include the following information: 1) Identification number, location, hand, fire rating, size, and material of each door and frame. 2) Locations of each door hardware set, cross-referenced to Drawings on floor plans and to door and frame schedule. 3) Complete designations, including name and manufacturer, type, style, function, size, quantity, function, and finish of each door hardware product. 4) Description of electrified door hardware sequences of operation and interfaces with other building control systems. 5) Fastenings and other pertinent information. 6) Explanation of abbreviations, symbols, and codes contained in schedule. 7) Mounting locations for door hardware. 8) List of related door devices specified in other Sections for each door and frame.
370 | 087100 | DOOR HARDWARE | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer
371 | 087100 | DOOR HARDWARE | 1.4-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For electrified door hardware, from the manufacturer. 1. Certify that door hardware approved for use on types and sizes of labeled fire-rated doors complies with listed fire-rated door assemblies.
372 | 087100 | DOOR HARDWARE | 1.4-C | INFORMATIONAL SUBMITTALS | Warranty | Warranty : Special warranty specified in this Section.
381 | 087100 | DOOR HARDWARE | 1.8-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer's standard form in which manufacturer agrees to repair or replace components of door hardware that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Structural failures including excessive deflection, cracking, or breakage. b. Faulty operation of doors and door hardware. c. Deterioration of metals, metal finishes, and other materials beyond normal weathering and use. 2. Warranty Period: Three years from date of Substantial Completion, unless otherwise indicated. a. Electromagnetic Locks: Five years from date of Substantial Completion. b. Magnetic Locks: Five years from date of Substantial Completion. c. Exit Devices: Two years from date of Substantial Completion. d. Manual Closers: Ten years from date of Substantial Completion.
382 | 087100 | DOOR HARDWARE | 3.6-A | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain door hardware and door hardware finishes.
383 | 087113 | POWER DOOR OPERATORS | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
384 | 087113 | POWER DOOR OPERATORS | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for power door operators. 2. Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.
385 | 087113 | POWER DOOR OPERATORS | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For power door operators. 1. Include plans, elevations, sections, hardware mounting heights, and attachment details. 2. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection. 3. Indicate locations of activation and safety devices. 4. Include diagrams for power, signal, and control wiring. 5. Include plans, elevations, sections, and attachment details for guide rails.
386 | 087113 | POWER DOOR OPERATORS | 1.5-C | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color and texture specified, manufacturer's standard size.
387 | 087113 | POWER DOOR OPERATORS | 1.6-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For power door operators, safety devices, and control systems, to include in maintenance manuals.
390 | 087113 | POWER DOOR OPERATORS | 1.8-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of power door operators that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Faulty or sporadic operation of power door operator, including controls. b. Deterioration of metals, metal finishes, and other materials beyond normal weathering or use. 2. Warranty Period: Two years from date of Substantial Completion.
394 | 087113 | POWER DOOR OPERATORS | 3.5-A | MAINTENANCE SERVICE | Maintenance Data | Initial Maintenance Service : Beginning at Substantial Completion, maintenance service shall include 12 months' full maintenance by skilled employees of power door operator Installer. Include quarterly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper door operation. Parts and supplies shall be manufacturer's authorized replacement parts and supplies. 1. Perform maintenance, including emergency callback service, during normal working hours. 2. Include 24-hour-per-day, seven-day-per-week, emergency callback service.
395 | 087113 | POWER DOOR OPERATORS | 3.6-A | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain power door operators.
402 | 088000 | GLAZING | 1.10-A | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty for Coated-Glass Products : Manufacturer agrees to replace coated- glass units that deteriorate within specified warranty period. Deterioration of coated glass is defined as defects developed from normal use that are not attributed to glass breakage or to maintaining and cleaning coated glass contrary to manufacturer's written instructions. Defects include peeling, cracking, and other indications of deterioration in coating. 1. Warranty Period: Ten years from date of Manufacture.
403 | 088000 | GLAZING | 1.10-B | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty for Laminated Glass : Manufacturer agrees to replace laminated- glass units that deteriorate within specified warranty period. Deterioration of laminated glass is defined as defects developed from normal use that are not attributed to glass breakage or to maintaining and cleaning laminated glass contrary to manufacturer's written instructions. Defects include edge separation, delamination materially obstructing vision through glass, and blemishes exceeding those allowed by referenced laminated-glass standard. 1. Warranty Period: Ten years from date of Manufacture.
404 | 088000 | GLAZING | 1.10-C | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty for Insulating Glass : Manufacturer agrees to replace insulating- glass units that deteriorate within specified warranty period. Deterioration of insulating glass is defined as failure of hermetic seal under normal use that is not attributed to glass breakage or to maintaining and cleaning insulating glass contrary to manufacturer's written instructions. Evidence of failure is the obstruction of vision by dust, moisture, or film on interior surfaces of glass. 1. Warranty Period: Ten years from date of Manufacture.
396 | 088000 | GLAZING | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
397 | 088000 | GLAZING | 1.5-B | ACTION SUBMITTALS | Samples | Glass Samples : For each type of glass product other than clear monolithic vision glass; 3 eax 12 inches square, as proposed for incorporation into the Project. 1. Tinted glass. 2. Laminated glass. 3. Insulating glass.
398 | 088000 | GLAZING | 1.5-C | ACTION SUBMITTALS | Samples | Glazing Accessory Samples : For sealants and colored spacers, in 12-inch lengths. Install sealant Samples between two strips of material representative in color of the adjoining framing system.
399 | 088000 | GLAZING | 1.5-D | ACTION SUBMITTALS | Schedules | Glazing Schedule : List glass types and thicknesses for each size opening and location. Use same designations indicated on Drawings.
405 | 092116.23 | GYPSUM BOARD SHAFT WALL ASSEMBLIES | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each component of gypsum board shaft wall assembly.
406 | 092216 | NON-STRUCTURAL METAL FRAMING | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
407 | 092216 | NON-STRUCTURAL METAL FRAMING | 1.4-A | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of code-compliance certification for studs and tracks.
408 | 092216 | NON-STRUCTURAL METAL FRAMING | 1.4-B | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For embossed, high-strength steel studs and tracks, firestop tracks, post-installed anchors and power-actuated fasteners, from ICC-ES or other qualified testing agency acceptable to authorities having jurisdiction.
410 | 092900 | GYPSUM BOARD | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
411 | 092900 | GYPSUM BOARD | 1.4-B | ACTION SUBMITTALS | Samples | Samples for Verification : For the following products: 1. Trim Accessories: Full-size Sample in 12-inch-long length for each trim accessory indicated.
412 | 092900 | GYPSUM BOARD | 1.5-A | QUALITY ASSURANCE | Mockups | Mockups : Build mockups of at least 100 sq. ft. in surface area to demonstrate aesthetic effects and to set quality standards for materials and execution. 1. Build mockups for the following: a. Each level of gypsum board finish indicated for use in exposed locations. 2. Apply or install final decoration indicated, including painting and wallcoverings, on exposed surfaces for review of mockups. 3. Simulate finished lighting conditions for review of mockups. 4. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
413 | 092900 | GYPSUM BOARD | 1.5-B | QUALITY ASSURANCE | Mockups | Coordinated Mockup : Before beginning gypsum board installation, install mockups of at least one door and window frame detail of each frame type that is installed flush ina gypsum board wall to demonstrate aesthetic effects and set quality standards for materials and execution. Coordinate with hollow metal frame supplier, coatings contractors, and sealant contractor where applicable. 1. Install mockups for the following: a. Door frame to be provided by Division 8 subcontractor and represent the flush frames that are proposed for the project. Frame to be provided by Division 8 suppliers and sealant by Division 7; all products to represent the units to be provided for the project. b. Flush glazed window units that are to be flush with gypsum board assemblies; frame and glazing to be provided by Division 8 suppliers and sealant by Division 7; all products to represent the units to be provided for the project. c. Wall finishes in CGMP spaces including wall covering/coatings on gypsum board with cove transition at ceiling and joint to ceiling plane with epoxy painted finish. d. High-performance coatings on hollow metal frames. e. Epoxy cove base detail(s) and associated trim. f. Electrical devices to be installed near door frame, i.e., light switches, access control, door actuators to represent installation with wall finishes. 2. Apply or install final decoration indicated, including painting or high performance coatings, wall covering, epoxy base and any required joint sealants, on exposed surfaces for review of mockups. 3. Simulate finished lighting conditions for review of mockups. 4. Construct mockup prior to ordering materials of construction so that dimensions can be confirmed and coordinated.
414 | 095123 | ACOUSTICAL TILE CEILINGS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
415 | 095123 | ACOUSTICAL TILE CEILINGS | 1.3-B | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color and texture specified, 6 inches in size.
416 | 095123 | ACOUSTICAL TILE CEILINGS | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each component indicated and for each exposed finish required, prepared on Samples of sizes indicated below: 1. Acoustical Tiles: Set of full-size Samples of each type, color, pattern, and texture. 2. Concealed Suspension-System Members: 6-inch long Sample of each type. 3. Exposed Moldings and Trim: Set of 6-inch- long Samples of each type and color. 4. Seismic Clips: Full size.
417 | 095123 | ACOUSTICAL TILE CEILINGS | 1.4-A | INFORMATIONAL SUBMITTALS | Coordination Drawings | Coordination Drawings : Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved: 1. Ceiling suspension-system members. 2. Structural members to which suspension systems will be attached. 3. Method of attaching hangers to building structure. a. Furnish layouts for cast-in-place anchors, clips, and other ceiling attachment devices whose installation is specified in other Sections. 4. Carrying channels or other supplemental support for hanger-wire attachment where conditions do not permit installation of hanger wires at required spacing. 5. Size and location of initial access modules for acoustical tile. 6. Items penetrating finished ceiling and ceiling-mounted items including the following: a. Lighting fixtures. b. Diffusers. c. Grilles. d. Speakers. e. Sprinklers. f. Access panels. g. Perimeter moldings. 7. Show operation of hinged and sliding components adjacent to acoustical tiles. 8. Minimum Drawing Scale: 1/8 inch = 1 foot.
418 | 095123 | ACOUSTICAL TILE CEILINGS | 1.4-B | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each acoustical tile ceiling, for tests performed by manufacturer and witnessed bya qualified testing.
419 | 095123 | ACOUSTICAL TILE CEILINGS | 1.4-C | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For each acoustical tile ceiling suspension system and anchor and fastener type, from ICC-ES.
420 | 095123 | ACOUSTICAL TILE CEILINGS | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For finishes to include in maintenance manuals.
421 | 095123 | ACOUSTICAL TILE CEILINGS | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Acoustical Ceiling Units: Full-size tiles equal to 2 percent of quantity installed, minimum of one full box of tile units.
425 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
426 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.3-B | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color and texture specified, not less than 12 inches long.
427 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of product indicated.
428 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.3-D | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of product indicated and for each color, texture, and pattern required in manufacturer's standard-size Samples, but not less than 12 inches long.
429 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.3-E | ACTION SUBMITTALS | Product Schedule | Product Schedule : For resilient base and accessory products. Use same designations indicated on Drawings.
430 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.4-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Furnish not less than 10 linear feet for every 500 linear feet or fraction thereof, of each type, color, pattern, and size of resilient product installed.
431 | 096723 | RESINOUS FLOORING | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
432 | 096723 | RESINOUS FLOORING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. Include manufacturer's technical data, application instructions, and recommendations for each resinous flooring component required.
433 | 096723 | RESINOUS FLOORING | 1.4-B | ACTION SUBMITTALS | Samples | Samples for Verification : For each resinous flooring system required, 6 inches square, applied toa rigid backing by Installer for this Project.
434 | 096723 | RESINOUS FLOORING | 1.4-C | ACTION SUBMITTALS | Product Schedule | Product Schedule : For resinous flooring. Use same designations indicated on Drawings.
435 | 096723 | RESINOUS FLOORING | 1.5-A | INFORMATIONAL SUBMITTALS | Certificates | Installer Certificates : Signed by manufacturer certifying that installers comply with specified requirements.
436 | 096723 | RESINOUS FLOORING | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each resinous flooring component, from manufacturer.
437 | 096723 | RESINOUS FLOORING | 1.5-C | INFORMATIONAL SUBMITTALS | Test Reports | Material Test Reports : For each resinous flooring system, bya qualified testing agency.
438 | 096723 | RESINOUS FLOORING | 1.6-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For resinous flooring to include in maintenance manuals.
442 | 096723 | RESINOUS FLOORING | 1.7-D | QUALITY ASSURANCE | Mockups | Mockups : Build mockups to verify selections made under Sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution. 1. Apply full-thickness mockups on 96-inch-square floor area selected by Architect. a. Include 96-inch length of integral cove base with inside and outside corner. 2. Simulate finished lighting conditions for Architect's review of mockups. 3. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing. 4. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
444 | 099123 | INTERIOR PAINTING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. Include preparation requirements and application instructions. 1. Include Printout of current "MPI Approved Products List" for each product category specified, with the proposed product highlighted. 2. Indicate VOC content.
445 | 099123 | INTERIOR PAINTING | 1.4-B | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of topcoat product.
446 | 099123 | INTERIOR PAINTING | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of paint system and in each color and gloss of topcoat. 1. Submit Samples on rigid backing, 8 inches square. 2. Apply coats on Samples in steps to show each coat required for system. 3. Label each coat of each Sample. 4. Label each Sample for location and application area.
447 | 099123 | INTERIOR PAINTING | 1.4-D | ACTION SUBMITTALS | Product Data | Product List : Cross-reference to paint system and locations of application areas. Use same designations indicated on Drawings and in schedules. Include color designations.
448 | 099123 | INTERIOR PAINTING | 1.5-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Paint: 5 percent, but not less than 1 gal. of each material and color applied.
449 | 099123 | INTERIOR PAINTING | 1.6-A | QUALITY ASSURANCE | Mockups | Mockups : Apply mockups of each paint system indicated and each color and finish selected to verify preliminary selections made under Sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution. 1. Architect will select one surface to represent surfaces and conditions for application of each paint system. a. Vertical and Horizontal Surfaces: Provide samples of at least 100 sq. ft. b. Other Items: Architect will designate items or areas required. 2. Final approval of color selections will be based on mockups. a. If preliminary color selections are not approved, apply additional mockups of additional colors selected by Architect at no added cost to Owner. 3. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing. 4. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
452 | 099600 | HIGH-PERFORMANCE COATINGS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. Include preparation requirements and application instructions. 1. Include printout of current "MPI Approved Products List" for each product category specified, with the proposed product highlighted. 2. Indicate VOC content.
453 | 099600 | HIGH-PERFORMANCE COATINGS | 1.4-B | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of topcoat product indicated.
454 | 099600 | HIGH-PERFORMANCE COATINGS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of coating system and each color and gloss of topcoat indicated. 1. Submit Samples on rigid backing, 8 inches square. 2. Apply coats on Samples in steps to show each coat required for system. 3. Label each coat of each Sample. 4. Label each Sample for location and application area.
455 | 099600 | HIGH-PERFORMANCE COATINGS | 1.4-D | ACTION SUBMITTALS | Product Data | Product List : Cross-reference to coating system and locations of application areas. Use same designations indicated on Drawings and in schedules. Include color designations.
456 | 099600 | HIGH-PERFORMANCE COATINGS | 1.5-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Coatings: 5 percent, but not less than 1 gal. of each material and color applied.
457 | 099600 | HIGH-PERFORMANCE COATINGS | 1.6-A | QUALITY ASSURANCE | Mockups | Mockups : Apply mockups of each coating system indicated to verify preliminary selections made under Sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution. 1. Architect will select one surface to represent surfaces and conditions for application of each coating system. a. Wall and Ceiling Surfaces: Provide samples of at least 100 sq. ft. b. Other Items: Architect will designate items or areas required. 2. Final approval of color selections will be based on mockups. a. If preliminary color selections are not approved, apply additional mockups of additional colors selected by Architect at no added cost to Owner. 3. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing. 4. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
461 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Equipment dimensions and weights (total assembled and operating)
469 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Single line interconnection diagram of all pieces of equipment
481 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Materials of construction
487 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Dimensions
490 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Cut sheets for all items for which design drawings will not be supplied. These must include dimensions, locations of piping/electrical connections, types of piping/electrical connections, material of construction, etc.
493 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Plan and elevation drawings for all components, which are assembled to achievea completed, functional piece of equipment and are not shown in adequate detail on the general arrangement type drawings.
495 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Identified parts list.
497 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Driver manufacturer's name
502 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Plan and elevation drawings for all components, with dimensions
507 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Terminal strip/wiring numbering
517 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Purchaser assigned instrument tag numbers.
524 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Detailed drawings indicating the shipping configuration of each equipment package or system. If the piece of equipment will be shipped in sub-sections, the drawings shall clearly indicate the boundaries, dimensions and weights of the sections.
529 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Location in both plan and elevation, of instrumentation installed on/around equipment.
537 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Piping interconnections
541 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Start date.
547 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Individual assembly weights (items, which are to be set in place as one entity).
550 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | Manufacturers Instructions | Installation and Start-up dates & duration
552 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | All utilities required by equipment.
554 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Complete set for each individual pressure vessel.
557 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Pump sizing
565 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Pumps
573 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Correct nomenclature to match drawings.
581 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Input/Output device name
588 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | All final approved drawings
600 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Description of equipment component being tested.
609 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Description of equipment component being inspected.
614 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Company information
627 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Description of electropolished equipment component
635 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Description of equipment component being passivated.
643 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Copies of manufacturer's calibration instructions.
646 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Description of equipment component being cleaned.
652 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Description of agitator being tested.
654 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-1 | SUBMITTALS | General | Printouts of documented, commented, source code. Comments are to include point, rung, and program level annotations.
478 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-10 | SUBMITTALS | General | Set points for relief valves, regulators, and control valves shall be indicated.
515 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-10 | SUBMITTALS | General | Intra-Panel wiring detail.
597 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-10 | SUBMITTALS | General | Complete spare parts and detailed parts list.
479 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-11 | SUBMITTALS | General | All hygienic clamp connections on critical system piping
516 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-11 | SUBMITTALS | General | Drawings shall differentiate between manufacturer and field installed wiring. A-12: INSTRUMENT SPECIFICATIONS Provide ISA style data sheets for every instrument supplied and include asa minimum:
598 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-11 | SUBMITTALS | Schedules | Lubrication schedules for all individual pieces of equipment, which are being supplied on the PO.
480 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-12 | SUBMITTALS | General | Notation necessary to adequately explain unique functions of specific items or subsystems, as required, and to add general clarity to the drawing. A-3: SCHEMATIC PIPING DIAGRAMS Drawings shall include:
599 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-12 | SUBMITTALS | Test Reports | List of all different types of acceptable lubricants, where used, and special handling and storage precautions. E-2: LEAK TEST REPORTS Provide reports that include the following:
462 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Equipment centerline
470 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Equipment description blocks for each piece of equipment on the drawing indicating, ata minimum, capacity, size, manufacturer, model number.
482 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Bill of materials
488 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Loading requirements w/relation toa reference point.
491 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | All sub-vendor's applicable mechanical, electrical, and instrumentation cut-sheets.
494 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | As-Builts | Bill of Materials for component or detail drawing A-7: AS-BUILT AND CERTIFIED EQUIPMENT DRAWINGS Provide certified drawings that reflect the as-built status for all drawings previously issued for review and approval. All drawings shall indicate the Owner's purchase order number, equipment item number, project number, description, National Board number when applicable, and manufacturer's serial number. Certified drawings shall be signed and dated by an authorized representative of the manufacturer of that component or system. A-8: MECHANICAL SEAL CROSS SECTION Drawings are required for all mechanical seals included in the scope of equipment package. Drawings shall include:
496 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | Bill Of Materials | Bill of materialsA-9 : VARIABLE FREQUENCY DRIVE (VFD) DATA SHEET Information required for all VFDs used on the equipment. Information shall include:
498 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Driver model number, catalog number, etc.
503 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Interior view including component layout information.
508 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Starters, overloads, protective devices
518 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Instrument type/service description
525 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Location and type of all rigging points.
530 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | Purchaser Assigned Instrumentation Tag Numbers.A-15 | Purchaser assigned instrumentation tag numbers.A-15 : INSTRUMENT LOOP DRAWINGS Provide loop drawings indicating information for each instrument loop containing all electrical and pneumatic piping connections:
538 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Electrical interconnections
542 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Start of engineering design.
548 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Individual units shipping weights.
551 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Copy of the procedures shall be delivered to the customer prior to the date of shipment to thecustomer.C-1 : UTILITY REQUIREMENTS Information to include:
553 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | Utility Operating Parameters Including | Utility operating parameters including : - a. pressure requirements b. pressure differentials and drops. c. peak and average flows d. temperature requirements e. total volume required per cycle. f. minimum quality requirement of utility g. heat dissipation from equipment h. electrical requirements i. drain requirements, flow, type, and size. j. biowaste drain requirements. k. humidity requirements and tolerances l. electromechanical and radio frequency interference (EMI/RFI) requirements m. all other environmental requirements, tolerances, and specifications C-2: ALLOWABLE FORCES AND MOMENTS ON NOZZLES Include information for all axis for all nozzles. C-3: ASME CODE CALCULATIONS Include:
555 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | Calculations | Reference Purchaser nozzle designations and services in calculations.
558 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Heat transfer and heat exchanger sizing
566 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Blowers
574 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Part numbers to match drawings/bill of materials.
579 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Part numbers to match drawings.
582 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Input/Output module tag numbers
589 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | All current equipment, instrument, and motor data sheets.
601 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Test date
628 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Electropolishing date
636 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Passivation date
644 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Required frequency of calibration (weekly, monthly, quarterly, yearly, etc.).
647 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Cleaning date
655 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-2 | SUBMITTALS | General | Electronic copies of source code listed above.
463 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Elevations referenced to finish floor elevation.
471 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | List of all plant/facility services required including sizes, capacities, temperatures, pressures, flow rates, etc.
483 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Type of connections with pipe sizes
489 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | Seismic Design InformationA-5 | Seismic design informationA-5 : CATALOG INFORMATION OF SUPPLIED COMPONENTS Information shall include:
492 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | Shop Drawings | Bill of materials A-6: DETAIL/SHOP DRAWINGS FOR COMPONENTS Drawings shall include:
499 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | Design Characteristics Including | Design characteristics including : - a. Efficiencies, hp, rpm, voltage, amperage, cycles, phase requirements b. Dimensions
504 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Wiring and pneumatic raceways
509 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Transformers
519 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Manufacturer/model number
526 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Indication of how all sub-sections will be re-joined, including all mating points and types of connections between systems.
531 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Reference P&ID number
539 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Instrument interconnections
543 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Proposed drawing cycle.
549 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | Manufacturers Instructions | Fully assembled erected weight of the completed assembly. B-3: INSTALLATION & START-UP SCHEDULE
556 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | Calculations | Seismic zone calculations C-4: SEISMIC CALCULCATIONS Provide seismic calculations performed to meet requirements where equipment will be installed. Calculations shall be sealed bya PE registered in that state. C-5: EQUIPMENT CALCULATIONS AND PERFORMANCE CURVES Provide calculations for instruments, equipment and specialty devises (if applicable) including:
559 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Pressure drop.
567 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Fans
575 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Quantity required.
583 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Input/Output devices' tag numbers
590 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Vendor data for all sub-vendor furnished equipment, valves, instrumentation, electrical components, etc.
602 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Start time.
611 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Company information
629 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | General | Start and finish times.
645 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | Reports | List of calibration instrumentation and/or tools necessary to perform the required calibrations. (Instrumentation utilized to perform this function shall be NIST traceable) E-15: CLEANING REPORT Provide reports that include the following:
656 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-3 | SUBMITTALS | Manufacturers Instructions | Application source code including file name, version, date generated, and serial number, where applicable. G-6: FACTORY ACCEPTANCE TEST PROTOCOLS AND TESTING PROCEDURES The protocol defines the details of the individual procedures and tests that will be performed. Vendor shall submita listing of standard tests performed witha brief description of the testing. Vendor shall submita detailed FAT protocol developed specifically for the purchased equipment for Purchasers review and approval prior to FAT testing. G-7: EXECUTED FAT PROTOCOL Provide all FAT documentation, including signed reports and test results. As applicable, provide the results for CIP spray device coverage tests for each piece of equipment, including test procedure and CIP conditions during tests. Document any test failures and subsequent correction steps. G-8: COMMISSIONING PLAN Provide Manufacturers recommended commissioning plan to support start-up and validation. G-9: VALIDATION PROTOCOLS Provide Manufacturers proposed installation qualification (IQ) and operational qualification (OQ) protocols for critical system equipment.
464 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Piping/electrical connections shall indicate type of connections, sizes, and locations including dimensions with reference points.
472 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Instrumentation and valves
484 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Special requirements such as slope
500 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Bill of materials
505 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Bill of Materials
510 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | All electrical components
520 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | Measurements | Range and units of measurement
527 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Bill of materials for assembly and/or arrangement drawings
532 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Original equipment manufacturers specification
540 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | Fabrication | Piece numbers for components requiring assembly. A-17: SPRAY DEVICE MAP After the spray device(s) are fabricated and successfully tested, provide the spray device map for each. B-1: PRODUCTION SCHEDULE A preliminary schedule, supplied with Quotation, shall include major fabrication milestone dates based upon Vendor's workload, understanding of scope of work, drawing review cycle, and requested delivery date. Asa minimum, schedule shall include:
544 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Completion of fabrication
560 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Agitator sizing
568 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Agitators
576 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Material of construction
584 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Input/Output hardware addresses
591 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | O&M Manuals | Detailed operating instructions with operating ranges, durations, settings, checklists, etc. for all supplied components.
603 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | End time
612 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Performed by signatures.
630 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Electropolishing settings
637 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Passivation temperature
648 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-4 | SUBMITTALS | General | Cleaning temperature
465 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Foundation requirements/plans
473 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Directions of flow/slope
485 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Directions of flow
501 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | Driver Tag Number (if Applicable)A-10 | Driver tag number (if applicable)A-10 : POWER & CONTROL PANEL DRAWINGS Drawings shall include:
506 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | Schedules | Nameplate schedules A-11: POWER AND CONTROL WIRING & PNEUMATIC DIAGRAMS AND SCHEMATICS Drawings shall include:
511 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Instrumentation (electrical/pneumatic connections)
521 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Reference P&ID number
528 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | Drawings | Sequence of assembly if not shown elsewhere.Provide dimensioned plan, elevation and section drawings, and isometric drawings as needed toclearly indicate this information.A-14 : INSTRUMENT LOCATION DRAWINGS Drawings shall include:
533 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | I/O address, as applicable
561 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Pressure vessel
569 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Vacuum Systems
577 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Manufacturers part number and nomenclature, when different (ifa buyout item)
580 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | Schedules | Manufacturers part number and nomenclature, when different D-3: DRAWING LIST Providea drawing list or index for all mechanical, electrical, instrumentation, P&ID, and misc. drawings, which will be issued / utilized for this PO. The list is to bea numbered list. Index should list all drawings, by title, in sequential order by drawing number, and indicate applicable document code identifier. Correct revision numbers shall also be included for all documents. D-4: INSTRUMENT LIST Provide an instrument list for all instrumentation. The list shall be in sequential order by tag number. The list shall include the tag number, data sheet number with current revision and date, instrument service description, P&ID number, line number, manufacturer, model number, part number, serial number (as applicable), maximum, minimum and tolerance. D-5: EQUIPMENT LIST Provide an equipment list for all major components. The list shall be in sequential order by tag number. The list shall include the tag number, data sheet number with current revision and date, service description, P&ID number, manufacturer, model, part number and serial number. D-6: VALVE LIST Providea valve list for all valves. The list shall be in sequential order by tag number. The list shall include the tag number, data sheet number with current revision and date, service description, P&ID number, line number, manufacturer, model number, serial number (as applicable), D-7: I/O SCHEDULE Include:
585 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Wire numbers for input/output modules
592 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Step by step startup, operating and shutdown procedures.
604 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Pressure at start
613 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | Test Reports | Inspection results E-5: TESTING AND CALIBRATION EQUIPMENT DATA Provide calibration procedures and current NIST traceable calibration certifications for all instruments used for calibration or testing of systems, including pressure gauges used for hydrostatic tests. E-6: PASSIVATION PROCEDURE Provide Vendors passivation procedure. These procedures shall include, asa minimum: the chemical composition of the detergents and passivation solutions to be used; the cleaning, passivation and rinse steps; test procedures to determine completeness of these steps; anda typical inspection and test reports. E-7: RIBOFLAVIN PROCEDURE Provide Vendors riboflavin procedure. These procedures shall include, asa minimum: the concentration of riboflavin solutions to be used; the riboflavin application and rinse steps; test procedures to determine completeness of these steps; anda typical inspection and test reports. E-8: CLEANING PROCEDURE Provide Vendors cleaning procedure. These procedures shall include, asa minimum: the chemical composition of the cleaning solutions to be used; the cleaning and rinse steps; procedures to determine completeness of these steps; anda typical inspection and procedure reports. E-9: VENDOR QA/QC PLAN Provide Vendors QA/QC Plan document E-10: VIDEO BOROSCOPE INSPECTION REPORT AND VIDEO DOCUMENTATION OF HYGENIC WELDS Refer to section 230500 Piping Materials and Methods 3.3.2 Weld/Brazing Inspections for borescope inspections and video requirements. Provide Inspection Report that includes the following:
618 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Description of equipment component inspected.
631 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Method of electropolishing contact, i.e., filled, submerged, swab, etc.
638 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Passivation solution and solution strength
649 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | General | Cleaning solution and solution strength
653 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-5 | SUBMITTALS | Test Reports | Test results E-17: FILTER CERTIFICATIONS: Provide manufacturer certification documentation (or C of C) for each filter provided with the equipment or system. E-18: VFD CONFIGURATION Provide all VFD configuration parameters (including parameters remaining as default). Parameter files can be electronic listing. F-1: WELD RECORDS Equipment records shall include the equipment description (name), manufacturer's name, part or model numbers, serial numbers and other relevant source identification information. Provide documentation per ASME BPE Latest Edition F-2: WELD PROCEDURE SPECIFICATIONS Provide documentation per ASME BPE Latest Edition F-3: PROCEDURE QUALIFICATION RECORD Provide documentation per ASME BPE Latest Edition F-4: WELDER PERFORMANCE QUALIFICATION Provide documentation per ASME BPE Latest Edition F-5: PURGE GAS CERTIFICATES Provide documentation per ASME BPE Latest Edition F-6: WELD MACHINE CALIBRATION REPORTS Provide documentation per ASME BPE Latest Edition F-7: WELDING OPERATOR PERFORMANCE QUALIFICATION Provide documentation per ASME BPE Latest Edition F-8: MATERIAL TEST REPORT Provide documentation per ASME BPE Latest Edition F-9: WELD COUPONS/LOGS Provide documentation per ASME BPE Latest Edition F-10: WELD WIRE/ROD MATERIAL DATASHEETS Provide documentation per ASME BPE Latest Edition F-11: WELD EXAMINER/INSPECTOR QUALIFICTIONS Provide documentation per ASME BPE Latest Edition G-1: SITE SPECIFIC SUPPORT PLAN Provide specific information regarding the manufacturers capability to respond to emergency service calls. Provide the quantity of available service technicians, including their discipline and their location and costs for warranty and non-warranty support. G-2: FUNCTIONAL DESIGN SPECIFICATION (FDS) Provide detailed information on the control system functionality including sequences, set points, interlocks, alarms, user interfaces, component interfaces, reporting, security, data handling, recipe handling, control hardware and software, and any other information required to describe and configure the overall control system. The FDS shall be written in accordance with the latest GAMP (Good Automated Manufacturing Practice) guidelines. G-3: HARWARE DESIGN SPECIFICATION (HDS) Providea control system HDS that includesa basic system description, memory type and capacity, I/O capacity, communications protocols, report generation, storage devices, and peripherals. Provide hardware specifications that include model numbers, part numbers, communication ports, memory and storage capacities, operating temperature and humidity ranges, power requirements, memory protection, environmental requirements, voltage spike protection, and RF protection. Also include the following: Programmer and User Interfaces Equipment Change Control and Compatibility Redundancy effects of component failures or power failures Component, wiring and terminal labeling. G-4: SOFTWARE DESIGN SPECIFICATION (SDS) Providea control system SDS that includes information on the programming software, system architecture, a detailed description of the system programming (including ladder logic if PLC based), all interlocks, alarms and control set points, I/O and memory addresses, test procedures, and any other information required to review and evaluate the design, as well as provide adequate direction for the development of the system programs. G-5 : SOFTWARE SOURCE CODES Provide source code documents including:
466 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Anchor bolt requirements including locations and sizes.
474 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Identification letters for all connection points to the equipment
486 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Identification letters for all connection points to the equipment.A-4 : FOUNDATION DIAGRAMS, LOADING REQUIREMENTS, AND SEISMIC DESIGN Drawings shall include:
522 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Original equipment manufacturers specification
534 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Field bus/devicenet device address, as applicable.
546 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | Fabrication | Estimated shipping time to jobsite. The production schedule shall be maintained and updated throughout the project. B-2: WEIGHT LIST OF FABRICATED PARTS FOR ERECTION, UNIT SHIPPING WEIGHT, ERECTED WEIGHTS Include:
562 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | Calculations | Atmospheric vessels (API calculations)
570 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Centrifuges
578 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Individual item/part's delivery time from date of order placement.D-2 : BILL OF MATERIALS (PARTS LIST W/PART NUMBERS) Include items installed to complete the purchased unit(s). Information required:
586 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Drawings
593 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Safety precautions during operation and/or maintenance of the equipment.
605 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Pressure at end
623 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | Measurements | Location and number of test points measured.
632 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Inlet water pH and final rinse water pH
639 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Method of passivation solution contact, i.e., filled, submerged, swab, circulation.
650 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-6 | SUBMITTALS | General | Method of cleaning solution contact, i.e., filled, submerged, swab, circulation.
467 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Clearances required for component removal.
475 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Equipment, instrument, and valve tag numbers
512 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Legend defining all abbreviations, components, & symbols
523 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Field bus/devicenet device address, as applicable.A-13 : ASSEMBLY AND/OR ARRANGEMENT DRAWINGS Drawings shall include:
535 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Description of test
563 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Refrigerant relief devices
571 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Motors with special starting or speed, torque or starting requirements.
587 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | O&M Manuals | Bill of materials including manufacturers model and serial numbers, where applicable D-8: ALARM AND INTERLOCK LIST Providea list for all alarms and interlocks. The list shall be in sequential order by description as shown on the screen. The list shall include all states of condition, trigger points and actions initiated. D-9: LIST OF SPECIAL TOOLS FOR MAINTENANCE AND/OR OPERATION Providea list of any special tools required to perform any startup production, and/or maintenance operations on the equipment being supplied on this PO. D-10: MATERIAL CERTIFICATION DATA Provide itemized parts list and materials of construction for all critical material items. Provide material inspection reports, shipping receipts, Certificates of Compliance, Mill Test Reports and other documents used in the execution of critical material handling. E-1: INSTALLATION, OPERATION AND MAINTENANCE MANUALS Manuals for each system shall be consolidated into an electronic file and shall include:
594 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | List of all routine, repetitive preventative maintenance procedures and frequencies.
606 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Test results
624 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | Measurements | Results of surface finish measurements.
633 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Performed by and witnessed by signatures with dates.
640 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-7 | SUBMITTALS | General | Inlet water pH and final rinse water pH
468 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | General | Leveling instructions or tolerances, and special handling instructions, if anyA-2 : FLOW DIAGRAMS OR PIPING & INSTRUMENTATION DIAGRAMS (P&IDs) Process/Piping and Instrumentation Diagrams (P&IDs) shall be provided for the main equipment package and any subsystems that comprise part of the overall equipment system. P&IDs shall follow ISA conventions as much as practical and possible, anda lead sheet indicating all symbology used on the P&IDs with descriptions shall be provided. P&IDs shall indicate the following asa minimum:
476 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | General | Size, material specification, service, insulation, and line number for all piping
513 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | General | Grounding
536 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | Drawings | Test resultsOne drawing shall be provided per loop. The drawings shall conform to ISA S5.1, S5.3, S5.4 and S5.5standards.A-16 : SYSTEM (SKID) INTERCONNECTION DETAILS Where equipment is supplied in multiple pieces/skids, drawing shall detail:
564 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | General | Control valvesProvide curves (if applicable) for :
572 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | General | Other equipment typically supplied with curves.C-6 : COMPLETED SPECIFICATION DATASHEETS Complete all fields identified as VS* (Vendor Specified), as well as indicating any fields where the specified data differs from the Manufacturer's offering. This work shall be done by hand directly on the data sheets ina legible and easily understood manner. The final data sheets which will become part of the final turn over package. D-1: RECOMMENDED SPARE PARTS LIST Provide recommended spare parts list for five (5) years normal maintenance: Include items to be purchased and recommended to be kept in stock in the manufacturing facility. These items are consumables such as fuses, gaskets, lamps, switches, belts, filters, etc., which need replacement ona frequent basis. The recommended spare parts list should also include items, which cannot be delivered to the manufacturing facility within 24 hours of verbal telephone order to the supplier. Information required:
595 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | General | List of all major preventative maintenance procedures and frequencies.
607 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | General | Company information
625 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | General | Model and serial number of test instrument used.
634 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | Reports | Company information E-13: PASSIVATION REPORT Provide reports that include the following:
641 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-8 | SUBMITTALS | General | Performed by and witnessed by signatures with dates.
477 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-9 | SUBMITTALS | General | A basic level of control system interconnects for all sensors, transmitters, and automated valves
514 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-9 | SUBMITTALS | General | Panel Layout
596 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-9 | SUBMITTALS | General | Step by step maintenance procedures for all required maintenance and/or repairs.
608 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-9 | SUBMITTALS | Calculations | Performed by signatures. E-3: ASME CODE CERTIFICATES/STAMPS/REPORTS Provide all applicable ASME forms (U-1, U-1A, U-2, U-3, and U-4), marking, weld inspection, and certification reports for all equipment and auxiliaries required to meet ASME codes and standards. Provide DIERS or ASME data and calculations of all temperature or pressure safety relief devices furnished with equipment or auxiliaries. E-4: INSPECTION REPORT Provide reports that include the following:
626 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-9 | SUBMITTALS | Reports | Calibration date of test instrument. E-12: ELECTROPOLISH REPORT Provide reports that include the following:
642 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-9 | SUBMITTALS | Company InformationE-14 | Company informationE-14 : CALIBRATION INSTRUCTIONS WITH INSTRUMENT RANGES, ACCURACIES AND TOLERANCES Include:
651 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 1.4.-9 | SUBMITTALS | Reports | Company information E-16: AGITATOR SHAFT RUN-OUT REPORT Provide reports that include the following:
657 | 110010 | EQUIPMENT GENERAL REQUIREMENTS | 2.1 | GENERAL | Product Data | All materials that will be incorporated into the final equipment package shall be new, unused, and undamaged unless otherwise specifically permitted in the specifications or authorized by the Owner. Refer to the main equipment specification and attachment drawings and specifications for the detailed design requirements for each equipment package. Equipment specifications for custom built equipment packages may be provided with varying levels of specification documentation, such as P&IDs, layout drawings, component data sheets, piping and instrumentation specifications and data sheets, equipment data sheets, etc. These documents are complementary. Where conflicts exist between these documents and this specification, the manufacturer shall submita request for clarification.
658 | 144600 | VERTICAL RECIPROCATING CONVEYOR | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : Submit latest edition of VRC data sheet and outline drawing with the proposal.
659 | 144600 | VERTICAL RECIPROCATING CONVEYOR | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Submit General Arrangement Drawing for approval within 3 weeks of receipt of an order, including plans, elevations, sections of the VRC, base plate and lateral loading values, and recommended pit dimensions if applicable. 2. Submit VRC Specification Sheet for approval within three weeks of receipt of an order, in- cluding scope of work, operating and control voltages, lift speed, type of paint, and any spe- cial project notes.
660 | 144600 | VERTICAL RECIPROCATING CONVEYOR | 1.5-C | ACTION SUBMITTALS | O&M Manuals | Closeout submittals provided with equipment : -
661 | 144600 | VERTICAL RECIPROCATING CONVEYOR | 1.5-C-1 | ACTION SUBMITTALS | O&M Manuals | Electrical Schematic Drawing including control panel layout and Bill of Materials reflect- ing original manufactured part numbers.
662 | 144600 | VERTICAL RECIPROCATING CONVEYOR | 1.5-C-2 | ACTION SUBMITTALS | Manufacturers Instructions | Installation Manual and Electrical Installation Guide.
663 | 144600 | VERTICAL RECIPROCATING CONVEYOR | 1.5-C-3 | ACTION SUBMITTALS | O&M Manuals | Owners Manual including spare parts list, exploded parts drawings, operating instructions, maintenance schedule, service and troubleshooting guidelines.
668 | 144600 | VERTICAL RECIPROCATING CONVEYOR | 1.7-A | WARRANTY | Warranty | The manufacturer shall warrant the VRC free of manufacturing defects beginning (30) days after shipment with the following minimums: 1. Structure lifetime parts and service 2. Manufactured components Five (5) years parts and labor 3. Purchased components Five (5) year parts, one (1) year labor.
672 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-1 | SUBMITTALS | Product Data | Product Data : Manufacturer's catalog cut sheets and other published technical data for each of the following: a. Nameplates, instructions plates, signs and labels. b. Fasteners.
673 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-2 | SUBMITTALS | Samples | Samples : Provide samples of each color, lettering style, and other graphic representation required for identification materials. Provide samples of labels and signs. No material is to be ordered without this approval.
674 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-3 | SUBMITTALS | Schedules | Providea listing of proposed names, abbreviations and other designations used in identification. Provide an electronic copy of the schedule of proposed tags, nameplates and engraving for Owner approval. No material is to be ordered without this approval.
675 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-4 | SUBMITTALS | General | Providea final and complete, electronic listing of all applied tags, nameplates and engravings.
676 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-5 | SUBMITTALS | Maintenance Data | Providea Hand Valve schedule as an electronic version in Microsoft Excel. Mark valves which are intended for emergency shut-off and similar special uses, by special flags, in margin of schedule. Furnish additional copies of schedule for Maintenance Manuals. Valve Schedule shall include the following information: a. Piping system b. System abbreviation (CW, CHWS, RO, WFI, etc.) c. Valve identification number d. Location of valve (room or space) e. Type of valve (gate, ball, automatic control, etc.) f. Manufacturer and manufacturer's catalog number g. Indicate valves intended for emergency shutoff or other special use
679 | 206305.01 | ENTER THE SPEC SECTION NAME | 1.9 | SUBMITTALS | General | The Vendor shall submita written control panel test procedure to the Owner for review and approval prior to executing the tests. The procedures shall detail installation inspection procedures, operation inspection procedures, and execution of these procedures. The Owner reserves the right to reproduce any drawing or print received from the Vendor, as may be required during the design and construction of this project and the preparation of the plant manual, despite any notice prohibiting the same appearing on the drawing or print. After the order is placed, the Vendor shall submit all data and drawings listed in the governing scope specification as issued with the Request for Quotation. The Owner job order number, purchase order number, project name, control panel name, and control panel identification number shall be shown on each drawing. The drawings submitted shall show the following asa minimum: General Arrangement drawings of the external and internal layouts, with Bill of Materials detailing responsibility of supply. Cross sections and details, as required, to satisfy the Owner that all components are in conformance with the intent of the specification and are satisfactory from the standpoint of design and physical arrangement. Internal control panel wiring diagrams showing terminal numbers, wire and cable labels, wire colors and gauge, and component labels. Pneumatic tubing layout, showing tubing labels and component labels. All information required by the Owner for design and location of all connecting furnished structural, mechanical, or electrical items such as foundations, steel supports, piping, ducts, cables, conduit, and so forth. Dimensions and weight of the equipment. 120 VAC power requirements, including FLA. After review by the Owner, a copy marked APPROVED, or REJECTED, REVISE AND RESUBMIT will be returned to the Vendor. If marked APPROVED, the Vendor may be directed to incorporate any changes per document mark-ups and/or attachments and resubmit to for record. If marked REVISE AND RESUBMIT, the required changes shall be incorporated by the Vendor and clearly identified, and the drawings shall again be submitted to the Owner for approval. If the Vendor elects not to incorporate the revisions, the Vendor shall inform the Owner that the suggested revisions cannot be made without prejudice to the Vendors responsibility under warranty. Arrangements for production scheduling shall not be deferred pending approval of drawings.
683 | 210900 | WET FIRE PROTECTION SYSTEMS | 1.2 | SUBMITTALS | General | Product Data for each type of sprinkler, valve, piping specialty, fire protection specialty, and fire department connections specified and/or provided. Shop Drawings prepared in accordance with FM Data Sheet 2-0 and NFPA 13 identified as Working Plans, and consistent with hydraulic calculations, and which have been approved by the authority having jurisdiction. Submit shop drawings showing piping materials, size, locations, and elevations. Include details of underground structures, connections, thrust blocks, and anchors. Show interface and spatial relationship between piping and proximate structures. Indicate hydraulic reference points corresponding to reference points indicated in hydraulic calculations. Hydraulic Calculations prepared in accordance with FM Data Sheet 2-0, 3-0, and NFPA 13, which have been approved by the authority having jurisdiction and owners insuring agency. Submit basic design information, sprinkler system requirements, water supply information including water supply and sprinkler system demand curves, and detailed worksheets. Indicate source of software and version used. Indicate hydraulic reference points corresponding to reference points indicated on shop drawings. Maintenance Data for each type of sprinkler, valve, piping specialty, fire protection specialty, fire department connection, hose and rack, and hose cabinet specified, for inclusion in operating and maintenance manual. Test Reports and Certificates including Contractor's Material & Test Certificate for Aboveground Piping and Contractor's Material & Test Certificate for Underground Piping as described in NFPA 13.
682 | 210900 | WET FIRE PROTECTION SYSTEMS | 1.4 | EXTRA MATERIALS....................................................................................................................... 2 | Attic Stock | PART 2. - PRODUCTS.......................................................................................................................................... 3
685 | 210900 | WET FIRE PROTECTION SYSTEMS | 1.4 | EXTRA MATERIALS | Attic Stock | Valve Wrenches: Furnish to Owner, two (2) valve wrenches for each type of sprinkler head installed. Sprinkler Heads and Cabinets: Furnish six (6) extra sprinkler heads of each style included in the project. Furnish each style with its own sprinkler head cabinet and special wrenches.
688 | 220411 | WATER DISTRIBUTION SPECIALTIES | 1.2 | SUBMITTALS | General | Product data for each item specified herein.
693 | 220440 | PLUMBING FIXTURES | 1.2 | EXTRA STOCK................................................................................................................................. 1 | Attic Stock | PART 2. - PRODUCTS.......................................................................................................................................... 1
695 | 220440 | PLUMBING FIXTURES | 1.2 | EXTRA STOCK | Attic Stock | Furnish one (1) each of any special wrenches and other devices necessary for servicing plumbing fixtures and trim to Owner. Furnish faucet repair kits complete with all necessary washers, springs, pins, retainers, packings, O-rings, sleeves, and seats ina quantity of one kit for each 40 faucets.
697 | 230010 | BASIC MECHANICAL REQUIREMENTS | 1.4 | WARRANTIES | Warranty | In addition to warranties called for in other sections of these specifications, work shall be warranted against defect due to faulty installation, manufacture, and component design. Warranties shall be fora period of not less than one (1) year, beginning on the later date of final acceptance by Owner, or equipment start-up. Upon written notice from the Owner or Engineer, promptly remedy, without cost to the Owner, any defects occurring or discovered during the warranty period.
698 | 230010 | BASIC MECHANICAL REQUIREMENTS | 1.5 | SUBMITTALS | General | General Provide submittals of material or equipment in accordance with the Submittal Requirement Schedule at the end of this specification section. Some sections have very specific submittal requirements, not indicated in this section, and therefore are indicated in that specific specification section. A submittal is required if an X is indicated for that column and item. Acceptable Manufacturers Subject to compliance with the requirements of the individual specification sections, provide materials and equipment from the indicated manufacturers only. Submittals of material or equipment manufactured by other than those indicated will be returned. If no manufacturers are indicated, then any product or material that complies with the specification and for the intended application is acceptable. If manufacturers are indicated, the first manufacturer in section list, or scheduled manufacturer or datasheet indicated manufacturer is the "basis of design", and all other indicated manufacturers are acceptable alternative manufacturers, as long as they also comply with the specification. It should be noted that there may be differences in dimension or installation requirements between the basis of design and others indicated and that additional work that may be required by other trades needs to be coordinated with the other trades and provided at no extra cost to the owner. Submittal Procedures Coordination: Coordinate preparation and processing of submittals with performance of construction activities. Transmit each submittal sufficiently in advance of performance of related construction activities to avoid delay. Coordinate each submittal with fabrication, purchasing, testing, delivery, other submittals and related activities that requires sequential activity. Coordinate transmittal of different types of submittals for related elements of the work so processing will not be delayed by the need to review submittals concurrently for coordination. The Owner or Owner's Representative reserves the right to withhold action ona submittal requiring coordination with other submittals until related submittals are received. Processing: Allow sufficient review time so that installation will not be delayed asa result of the time required to process submittals, including time for resubmittals. Allow ten working days for initial review. Allow additional time if processing must be delayed to permit coordination with subsequent submittals. The Owner or Owner's Representative will promptly advise the Contractor whena submittal being processed must be delayed for coordination. If an intermediate submittal is necessary, process the same as the initial submittal. Allow ten working days for reprocessing each submittal. No extension of contract time will be authorized because of failure to transmit submittals to the Owner or Owner's Representative sufficiently in advance of the work to permit processing. Submittal Preparation: Placea permanent label or title block on each submittal for identification. Indicate the name of the entity that prepared each submittal on the label or title block. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Contractor's review and approval markings and the action taken. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Owner's or Owner's Representative review and approval markings and the action taken. Include the following information on the label or title block for processing and recording action taken. Project name Date Name and address of Owner Name and address of Engineer Name and address of Contractor Name and address of subcontractor Name and address of supplier Name of manufacturer Number and title of appropriate Specification Section Drawing number and detail references, as appropriate Unique Submittal Number for each package Submittal Transmittal: Package each submittal appropriately for transmittal and handling. Transmittal shall list specification section for each item submitted. Transmit each submittal from Contractor to Owner or Owner's Representative usinga transmittal form. Submittals received from sources other than the Contractor will be returned without action. Submittals: Submit one (1) electronic copy of each required submittal ina single combined PDF format with all individual specification sections separated individually. The Engineer will mark and return one (1) electronic copy in PDF format with action taken and corrections or modifications required. Owner will retain one (1) electronic copy of returned document. Retain copy of each for O&M manuals or Enhanced Turn Over Packages (ETOPs). Schedules: Project schedules indicating proposed work phases and sequences. Include in schedule asa minimum, approvals, equipment release, delivery, fabrication, equipment setting, startup, punch, and cleanup. Submittal Schedule Prepare and submita complete schedule of submittals. Coordinate submittal schedule with the construction schedule. Prepare the schedule in chronological order. Provide the following information: Scheduled date for submittal Related Section number Submittal category Name of subcontractor Description of the part of the work covered Anticipated date for Engineer's final release or approval Schedule Updating: Revise the schedule after each meeting or activity, where revisions have been recognized or made. Issue the updated schedule to all parties involved. 1.5.1. Review Action The Contractor is responsible for all data and information on submittals, including quantities, sizes, dimensions, and compliance with the Drawings and Specifications. Checking by the Owner or Owner's Representative is only for general conformance with the design concept of the project and general compliance with the information given in the Contract Documents. Any action shown is subject to the requirements of the Drawings and Specifications. Contractor is responsible for dimensions and quantities, which shall be confirmed at the job site, and fabrication process and techniques of construction. On the submittal, record relevant information and requests for data. Record deviations from Contract Document requirements, including minor variations and limitations. Include Contractor's certification that information complies with Contract Document requirements. Except for submittals for record, information for similar purposes, where action and return is required or requested, the Owner will check each submittal, mark to indicate action taken, and return promptly. Compliance with specified characteristics is the Contractor's responsibility. 1.5.2. Shop Drawings Submit information, drawn to accurate scale. Highlight, encircle, or otherwise indicate deviations from the Contract Documents. Do not reproduce Contract Documents or copy standard information as the basis of Shop Drawings. Standard information prepared without specific reference to the Project is not considered Shop Drawings. Shop Drawings include fabrication and installation drawings, setting diagrams, schedules, patterns, templates and similar drawings, and directions for installation of anchorages. Include asa minimum the following information on drawings or diagrams: Dimensions Identification of products and materials included Compliance with specified standards Notation of coordination requirements Notation of dimensions established by field measurement Clearances for access and service Sheet Size: Except for templates, patterns and similar full-size drawings, submit Shop Drawings in PDF format at least 8" x 11", but no larger than 30" x 42". Initial Submittal: (Where Contractor desires product specific information or preliminary review prior to processing of final submittal.) Submit an electronic copy of prints in PDF format for the Owner's review. Final Submittal: Submit electronic copy of all prints. An electronic set of prints will be retained and maintained asa Record Document. The Owner's representative has the right to mark up the final submittal. Do not use Shop Drawings without an appropriate final stamp indicating action taken in connection with construction. 1.5.3. Coordination Drawings or 3D (BIM) Model: Mechanical, Electrical, Plumbing and Fire Protection Contract Drawings or 3D (BIM) model are diagrammatic. They are not intended to be precise; they are not intended to specify or to show every offset, fitting, and component. The purpose of the drawings or 3D (BIM) model is to indicatea systems concept, the main components of the systems, and the approximate geometrical relationships. Information and components shown on diagrams, but not shown on plans, and vice versa, shall apply or be provided as if expressly required on both. The contractor shall provide coordination drawings or 3D (BIM) model; detailing major elements, components, and systems of mechanical equipment and materials in relationship with other systems, installations, and building components. Indicate locations where space is limited for installation and access and where sequencing and coordination of installations are of importance to the efficient flow of the Work. Drawings or 3D (BIM) model shall include but shall not be limited to the following: Clearances for installing and maintaining installation. Clearances for servicing and maintaining equipment, including tube removal, filter removal, valves and space for equipment disassembly required for periodic maintenance. Equipment connections and support details. Exterior wall and roof penetrations. Fire-rated wall and floor penetrations. Sizes and locations of required concrete pads and bases. Valve stem movement. Plumbing systems, piping and equipment. HVAC piping, systems and equipment. Process piping,
700 | 230125 | EXPANSION COMPENSATION | 1.4 | SUBMITTALS................................................................................................................................... 2 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
702 | 230125 | EXPANSION COMPENSATION | 1.4 | SUBMITTALS | General | Submittals shall be specific to this equipment and components with detail drawings provided showing actual materials of construction, dimensions and connection sizes. The submittals shall include data sheets for all components and evidence of EJMA certification. Provide all load and thrust forces to be exerted on the building structure for approval by the structural engineer. Provide shop drawing indicating all expansion devices, guides and anchors along with calculations showing that the stresses do not exceed the piping stresses allowed and prevent transfer of loading and stresses to connected equipment. Analysis shall be signed and sealed by the qualified professional engineer responsible for their preparation. Delegated Design: The anchor, guide and expansion joints have been preliminarily indicated on the plans. The contractor shall finalize the design and selection based on final piping layout and job site conditions. The final selection and locations shall be submitted with calculations and shall be signed and sealed bya Professional Engineer, registered in the State of the project, who hasa minimum of 5 years of piping design experience. Final selection and details shall indicate the movement of the piping as well as the forces on the anchors and the guides to maintain motion in the intended direction.
703 | 230140 | HANGERS AND SUPPORTS | 1.5 | SUBMITTALS................................................................................................................................... 2 | General | PART 2. - PRODUCTS.......................................................................................................................................... 3
705 | 230140 | HANGERS AND SUPPORTS | 1.5 | SUBMITTALS | General | Provide submittal documents in compliance with requirements indicated in specification 230010. Provide drawings of each pipe hanger assembly and equipment support for each system application. Delegated-Design Submittal: For trapeze hangers and equipment supports indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation. Detail fabrication and assembly of trapeze hangers and equipment supports. Design Calculations: Calculate requirements for designing trapeze hangers and equipment supports.
707 | 230241 | VIBRATION AND SEISMIC CONTROLS | 1.5 | SUBMITTALS | General | Product Data Include rated load, rated deflection, and overload capacity for each vibration isolation device. Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of seismic- restraint component used. Tabulate types and sizes of seismic restraints, complete with report numbers and rated strength in tension and shear as evaluated by an agency acceptable to authorities having jurisdiction. Annotate to indicate application of each product submitted and compliance with requirements. Interlocking Snubbers: Include ratings for horizontal, vertical, and combined loads. Delegated-Design Submittal: For vibration isolation and seismic-restraint details indicated to comply with performance requirements and design criteria, including analysis data. Design shall be signed and sealed by the qualified professional engineer responsible for their preparation. Note professional engineer must be registered in the same state as the project work. Design Calculations: Calculate static and dynamic loading due to equipment weight and operation, seismic and wind forces required to select vibration isolators, seismic and wind restraints, and for designing vibration isolation bases. Coordinate design calculations with wind load calculations required for equipment mounted outdoors including, but not limited to: Cooling Towers, Exhaust Fans, Condensing Unit, and Air handling units. Comply with requirements in other Division 23 Sections for equipment mounted outdoors. Riser Supports: Include riser diagrams and calculations showing anticipated expansion and contraction at each support point, initial and final loads on building structure, spring deflection changes, and seismic loads. Include certification that riser system has been examined for excessive stress and that none will exist. Vibration Isolation Base Details: Detail overall dimensions, including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails, base weights, equipment static loads, power transmission, component misalignment, and cantilever loads. Seismic and Wind Restraint Details Design Analysis: To support selection and arrangement of seismic and wind restraints. Include calculations of combined tensile and shear loads. Details: Indicate fabrication and arrangement. Detail attachments of restraints to the restrained items and to the structure. Show attachment locations, methods, and spacings. Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during seismic events. Indicate association with vibration isolation devices. Coordinate seismic-restraint and vibration isolation details with wind-restraint details required for equipment mounted outdoors. Comply with requirements in other Division 23 Sections for equipment mounted outdoors. Preapproval and Evaluation Documentation: By an agency acceptable to authorities having jurisdiction, showing maximum ratings of restraint items and the basis for approval (tests or calculations). Coordination Drawings: Show coordination of seismic bracing for HVAC piping and equipment with other systems and equipment in the vicinity, including other supports and seismic restraints. Welding certificates Qualification Data: For professional engineer and testing agency. Field Quality-Control Test Reports
711 | 230275 | PRESSURE SAFETY RELIEF DEVICES | 1.4 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
713 | 230275 | PRESSURE SAFETY RELIEF DEVICES | 1.4 | SUBMITTALS | General | Provide submittal documents in compliance with requirements indicated in Section 230010 Basic Mechanical Requirements.
714 | 230480 | HYGIENIC SYSTEM SPECIALTIES | 1.4 | SUBMITTALS................................................................................................................................... 2 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
716 | 230480 | HYGIENIC SYSTEM SPECIALTIES | 1.4 | SUBMITTALS | General | Provide submittal documents in compliance with requirements indicated in specification section 230010.
717 | 230500 | PIPING MATERIALS AND METHODS | 1.4 | SUBMITTALS................................................................................................................................... 2 | General | PART 2. - PRODUCTS.......................................................................................................................................... 3
719 | 230500 | PIPING MATERIALS AND METHODS | 1.4 | SUBMITTALS | General | Provide submittal documents in compliance with requirements indicated in specification section 230010 for each piping system in the Piping System Application Table. For equipment procured prior to the Issued for Construction set of documents, provide submittal documents in compliance with requirements indicated in specification section 110010 for each piping system in the Piping System Application Table. In addition, provide welders' certifications, and all documentation as required by each associated code sections identified in the Piping System Application Table. Prior to fabrication of piping systems identified with either ASME BPE, ASME B31.3, or ASME B31.12 in the Piping System Application Table, provide detailed shop drawings of the piping installation, including isometrics of the piping system, which illustrates all fittings, equipment connections, instruments, valves, and welds shall be submitted for approval. Each isometric shall include direction of slope, critical dimensions, and system elevation and location measurements. All isometrics shall be drawn from the same perspective with relationship to the building, unlessa different perspective would provide more detail or better clarification. Prior to fabrication of piping systems, the Contractor shall note in detailed shop drawings and isometrics where deviations occur between Engineering drawings and Contractor isometrics and/or shop drawings. Changes requiring piping stress analysis rework will be responsibility of the Contractor. For systems identified as ASME BPE in the Piping System Application Table, Contractor shall submit for Owner and Engineering approval the Material and Weld Examination/Inspection Documentation prepared for the project. If the Contractor does not have standard forms to submit, the Contractor may utilize the forms in the Appendix B section of ASME BPE as their submission. At completion of work, provide record "As-Built" copies of system drawings indicated as ASME BPE, ASME B31.3, or ASME B31.12 for inclusion in Owners files for validation. Refer to Piping System Application Table to determine systems required to be validated. Include weld numbers in final As-Built drawings where applicable.
741 | 230510 | HYDRONIC SYSTEM SPECIALTIES | 1.2 | SUBMITTALS | General | Product data for each item specified here-in.
740 | 230510 | HYDRONIC SYSTEM SPECIALTIES | 1.4 | EXTRA MATERIALS....................................................................................................................... 1 | Attic Stock | PART 2. - PRODUCTS.......................................................................................................................................... 1
743 | 230510 | HYDRONIC SYSTEM SPECIALTIES | 1.4 | EXTRA MATERIALS | Attic Stock | For each type of balancing valve and automatic flow control valve, provide flowmeter, probe, hoses, flow charts and carrying case. Turn over to Owner at system start-up/turnover.
744 | 230520 | STEAM SYSTEM SPECIALTIES | 1.3 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
746 | 230520 | STEAM SYSTEM SPECIALTIES | 1.3 | SUBMITTALS | Product Data | Product Data: Submit product data for each item included. Submit calculations and sizing data for all pressure reducing valves and safety relief valves.
748 | 230526 | CONDENSATE HANDLING EQUIPMENT | 3.3 | TRAINING | O&M Training And Demonstration | Train the Owner's personnel on start-up and shutdown procedures, troubleshooting procedures, and servicing and preventative maintenance schedules and procedures. Review the data in the Operating and Maintenance Manuals, with the Owner's authorized personnel. Schedule training with Owner and provide at least seven (7) days notice to Owner prior to training date. Providea manufacturer's technical representative for one (1) eight-hour day to train the Owner's personnel.
749 | 230540 | PUMPS | 1.3 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
751 | 230540 | PUMPS | 1.3 | SUBMITTALS | General | Reference specification section 230010 Basic Mechanical requirements for submittal requirements in addition to those indicated in this section. 1.3.1. Completed Data Sheets The Vendor/Manufacturer shall complete all fields indicated as VS* (Vendor Specified) on each data sheet, as well as correct/modify any other fields and values as required, and submit them with the initial bid, and as part of the final submittal documentation. 1.3.2. Hygienic Pumps Hygienic pumps are those that are indicated as required to comply with ASME BPE on the data sheets. Hygienic pumps will be used for critical biopharmaceutical systems (product contact, USP compendial water, CIP, etc.), and shall comply with all applicable requirements of ASME BPE, including the following GMP documentation requirements: Surface Finish Certifications Certificates of Compliance Manufacturer's Data and Test Reports Non-Destructive Examination (NDE) Reports The Vendor/Manufacturer shall provide documentation verifying the wetted materials of construction meet the requirements indicated in the specifications.
753 | 230540 _revised_663 | CENTRIFUGAL PUMP | 7.0 | NOZZLE SCHEDULE | Schedules | Equipm nt Power 480 V, 3 Ph, 60 Hz TBD Amps VS* Amps VS* Amps
754 | 230755 | HEAT EXCHANGERS | 1.4 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2 PART 3. - EXECUTION........................................................................................................................................ 2
756 | 230755 | HEAT EXCHANGERS | 1.4 | SUBMITTALS | General | Reference specification section 230010 Basic Mechanical requirements for submittal requirements in addition to those indicated in this section. Completed Data Sheets The Vendor/Manufacturer shall complete all fields indicated as VS* (Vendor Specified) on each data sheet, as well as correct/modify any other fields and values as required, and submit them with the initial bid, and as part of the final submittal documentation. Hygienic Heat Exchangers Hygienic heat exchangers are units that will be used for critical biopharmaceutical systems (product contact, USP compendial water and steam, etc.), and which shall comply with all applicable requirements of ASME BPE, including weld, material and testing documentation. Tube samples from the U-bend portions of U-tube heat exchangers shall be submitted for review and approval per ASME BPE requirements. Inlet and outlet nozzle design shall be coordinated with the installation of the piping. Submit piping to and from heat exchanger for approval, showing all high point and low points and documentation to show complete drain- ability of the heat exchanger and attached piping. Shell and Tube Heat Exchangers The Manufacturer shall submita completed TEMA sheet indicating all operational parameters of each unit with the initial bid, and as part of the final submittal documentation.
760 | 230855 | CUSTOM AIR HANDLING UNITS | 1.3 | SUBMITTALS | General | Bid alternate and selection matrix for owner and engineer review. Product data shall include dimensions, weights, capacities, certifications, component performance, electrical characteristics, casing construction details, wiring interconnections, gauges and material finishes. The submittal shall provide all technical information relevant to the product being provided, including but not limited to, all the information shown in the attached data sheet and equipment schedules. It is the responsibility of the supplier to highlight any variances the equipment has with the requirements of this specification whether or not pre-approval has been obtained. Information shall be provided in the same measurement units as indicated in the data sheet and equipment schedules. The submittal(s) shall provide independent fan curves for operating/design conditions, with specified operating/design points clearly plotted. The submittal(s) shall provide coil selection worksheets, clearly showing proper consideration for altitude, air density, glycol corrections and indicate coil tube fin and casing construction. The submittal(s) shall provide filter information, including initial (clean) APD, final (dirty) APD, dust spot efficiency, final dust holding capacity, filter media description, filter frame details, and filter removal details. The manufacturer shall submit sound power levels for both air handling unit inlet, outlet and radiated at rated capacity. The manufacturer shall submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring. The manufacturer shall submit the manufacturers recommended installation instructions. Omission of any of the above information will cause shop drawings to be immediately returned without review.
761 | 230855 | CUSTOM AIR HANDLING UNITS | 1.4 | OPERATION AND MAINTENANCE DATA | O&M Manuals | The manufacturer shall submit operation and maintenance data under provisions of Section 230501. The manufacturer shall include instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists, and wiring diagrams.
758 | 230855 | CUSTOM AIR HANDLING UNITS | 1.5 | WARRANTY..................................................................................................................................... 2 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 2
762 | 230855 | CUSTOM AIR HANDLING UNITS | 1.5 | WARRANTY | Warranty | Provide warranty in compliance with Section 230010.
764 | 230855 | CUSTOM AIR HANDLING UNITS | 3.7 | EXTRA FILTER STOCK | Attic Stock | The manufacturer or contractor will provide one extra set of pre-filters for each air handling unit. Install new filters at completion of air handling system work, and prior to testing, adjusting, and balancing work. Obtain receipt from testing and balancing contractor that new filters have been installed.
765 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 1 | SCHEDULES | Schedules | Provide manufacturers one (1) year warranty. Warranty period shall begin at equipment start-up or six months after delivery, whichever occurs first.
774 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 10 | SCHEDULES | Schedules | Insulation shall havea flame spread rating of 25 anda smoke developed rating of 50.
775 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 11 | SCHEDULES | Schedules | Providea flanged connection for all duct connections to the unit (i.e. supply air, return air, outside, air, relief air)
776 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 12 | SCHEDULES | Schedules | Maximum wall or roof deflection shall not exceed L/200 at 8 of static pressure. Maximum leakage shall not exceed 1% of unit capacity at 125% of design static pressure. Maximum live load floor deflection shall not exceed the lesser of L/360 and 1/2 inch and floor shall be suitably braced to prevent "oil canning."
777 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 13 | SCHEDULES | Schedules | Units will be located on the roof which will be exposed to outdoor air conditions of 82F db / 72F wb. Design of air handling units shall be such that air handling unit casing will not cause condensation.
778 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 14 | SCHEDULES | Schedules | Each unit/module shall be supplied with four (4) lifting points ata minimum. Manufacturer to provide lifting lugs and bracing for each unit/module.
779 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 15 | SCHEDULES | Schedules | Provide piezometer ring on fan inlet with flow transmitter at accuracy above.
780 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 16 | SCHEDULES | Schedules | Select fans for both conditions of 4 fans operating and 3 fans operating. Ensure proper wheel diameter and percent wheel width for acceptable RPM and acceptable location on the static pressure curve for both conditions.
781 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 17 | SCHEDULES | Schedules | Pressure transmitters and displays and other gauges with readings need to be at an accessible height for visual checks on AHU mounted on curb by operator standing on the roof without use ofa ladder or stool. UNIT LAYOUT: Left Side 1 2 3 4 5 6 Right Side Section # Section Type 1 Mixing Box w/ Access 2 Filter Section w/ Access 3 Cooling Coil Section w/ Access 4 Heating Coil Section w/ Access 5 Supply Fan Array 6 Supply Air Plenum w/Access Side of Unit for Access Left Side of Unit for Piping Connections Left
766 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 2 | SCHEDULES | Schedules | Provide one (1) extra set of filters for installation by contractor prior to final balancing.
767 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 3 | SCHEDULES | Schedules | Sealants shall be non-sag, non-staining, permanently flexible, of the highest quality and recommended by its manufacturer for the intended application. Sealant (gasket) materials shall not be reactive, additive, or absorbtive so as to alter the air (fluid) stream.
768 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 4 | SCHEDULES | Schedules | Unit and components shall be selected for design conditions specified above and then manufacturer shall provide operating performance for unit and components selected.
769 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 5 | SCHEDULES | Schedules | Providea spare parts list anda firm quote price for spare parts. VS * - Vendor/Manufacturer to Supply Information Project No 206305.01 Page 5 of 7 CRB Consulting Engineers, Inc.
770 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 6 | SCHEDULES | Schedules | Unit shall be fully performance tested at site after installation, for coil performance, housing leakage rate, and fan performance. Manufacturer shall replace or correct any components not meeting project specifications.
771 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 7 | SCHEDULES | Schedules | Unit manufacturer shall providea qualified service technician for start-up of unit and to instruct Owner's personnel fora minimum of eight (8) hours on maintenance and operation of unit.
772 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 8 | SCHEDULES | Schedules | Unit shall be thoroughly cleaned to remove all dust, grease, excess sealant, and other debris. All openings shall be sealed airtight prior to shipment.
773 | 230855 _revised_697 | CUSTOM AIR HANDLING UNITS | 9 | SCHEDULES | Schedules | Owner approved equivalent filters may be provided in lieu of filters, specified above.
782 | 230860 | FANS | 1.4 | WARRANTY..................................................................................................................................... 1 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 1
784 | 230860 | FANS | 1.4 | WARRANTY | Warranty | Provide warranty in accordance with Section 230010.
787 | 230891 | METAL DUCTWORK | 1.5.-1 | DUCTWORK SUBMITTALS | General | Sheet metal fabrication drawings at minimum 3/8 = 1-0 scale.
788 | 230891 | METAL DUCTWORK | 1.5.-2 | DUCTWORK SUBMITTALS | General | Ductwork material and fabrication standards indicating gauges, seam and joint construction details, reinforcing details and spacing, and fittings for the various pressure classifications required.
789 | 230891 | METAL DUCTWORK | 1.5.-3 | DUCTWORK SUBMITTALS | Product Data | Sealing materials product data
790 | 230891 | METAL DUCTWORK | 1.5.-4 | DUCTWORK SUBMITTALS | Product Data | Fire-stopping materials product data
791 | 230891 | METAL DUCTWORK | 1.5.-5 | DUCTWORK SUBMITTALS | General | Hangers and supports, including methods for building attachment, vibration isolation, and duct attachment.
792 | 230891 | METAL DUCTWORK | 1.5.-6 | DUCTWORK SUBMITTALS | General | Duct accessories, including access doors and panels. Provide coordination drawings of ductwork in collaboration with all other trades in accordance with specification section 230010.
799 | 230910 | DUCTWORK ACCESSORIES | 1.4 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
801 | 230910 | DUCTWORK ACCESSORIES | 1.4 | SUBMITTALS | Product Data | Product Data: For each type of product indicated. Shop Drawings: Indicate installation details in ductwork and other construction. Provide wiring diagrams.
803 | 230932 | AIR OUTLETS AND INLETS | 1.4 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
804 | 230932 | AIR OUTLETS AND INLETS | 1.4 | SUBMITTALS | Product Data | Product Data: For each type of product indicated, include the following: Indicate materials of construction, finish, and mounting details; and performance data including throw and drop, static-pressure drop, accessories and noise ratings. It is the responsibility of any manufacturer providing submittals to verify in advance their performance criteria is similar to Basis of Design (BOD) manufacturer in the following criteria. General compatibility- style, construction, ceiling or wall integration, fastening, color and accessories. Performance: NC level shall be equal to or less than BOD. Static and total pressure shall be equal to or less than BOD. Isothermal throw data at 150/100/50 fpm shall be within plus or minus 5% of the BOD values for standard products. Air devices for critical spaces shall be shown with cooling temperature differentials of 5/10/15 degrees and throws of 100/75/50/30 fpm. Data shall be presented by computerized selection software. Catalog charts and graphs are not acceptable unless the tabular data is rated within 10% of the BOD performance selected. Manufacturers not complying with all portions of requirements will be rejected and not subject to further review by the design professional.
805 | 230932 | AIR OUTLETS AND INLETS | 3.5 | SPARE PARTS | Attic Stock | Furnish to Takeda, with receipt, three operating keys for each type of air outlet and inlet that require them.
807 | 230970 | CONTROL SYSTEMS | 1.7 | SUBMITTALS WITH BID | General | System Architecture Drawing: Submit drawing indicating overall network of DDC Controllers, Application Specific Controllers, Computer(s), Printers and all major system components indicating how they are networked, how many Controllers are being provided and what they Control.
808 | 230970 | CONTROL SYSTEMS | 1.8 | SUBMITTALS AFTER AWARD OF CONTRACT | Product Data | Product Data: Submit one (1) electronic (PDF format) of manufacturer's technical product data for each control device and instrument furnished, indicating dimensions, capacities, performance, accuracy, electrical characteristics and material finishes. Final approved submittals, as-built drawings and installation and maintenance data shall be easily accessible through the BAS system. Provide complete Control Valve schedule indicating valve type, model number, size, Cv and maximum shutoff pressure. Provide complete Control Damper schedule indicating damper type, model number, size and torque required. Shop Drawings: Submit one (1) electronic (PDF format) of shop drawings for control system containing the following information. Any product or work indicated on drawings that is not provided by the Controls Contractor shall be clearly identified. Schematic flow diagram of system indicating fans, pumps, coils, dampers valves, and control devices as applicable to project. Instrument location plans showing the location of all panels and field devices. Details of control panels, including panel layout, controls, instruments, labeling and bill of materials. Point names and addresses for each control device labeled with setting or adjustable range of control. All required wiring including terminal identification. Clearly differentiate between portions of wiring that are factory-installed and portions to be field-installed. Provide cable schedule with complete termination details for field-installed wiring. Graphical User Interface Screens: Submit one (1) electronic (PDF format) of proposed graphic screens in color with written notation indicating how the screen will operate dynamically. Sequence of Operations: Submit Sequence of Controls for each system as indicated in Related Documents. System Manuals: Provide one (1) electronic (PDF format) bookmarked set of system Operating and Maintenance manuals which shall contain, asa minimum, the following: 1. Index sheet, listing contents in alphabetical order. 2. Manufacturer's equipment parts list of all functional components of the system, Auto-CAD disk of system schematics, including wiring diagrams. 3. System Schematic diagrams with written description of Sequence of Controls. 4. As-Built interconnection wiring diagrams. 5. Operator's Manual. 6. System Network Architecture Drawing showing remote electronic panel locations and all trunk data. 7. List of connected data points, including panels to which they are connected and input device (ionization detector, sensors, etc.). Maintenance Data: Submit maintenance instructions and spare parts lists for each type of control device. Include installation, calibration and start-up instructions. Record Drawings: Upon completion of the work, providea complete set of record drawings indicating the BAS system as installed. Drawings shall be provided as AutoCAD (latest version) files in hard copy and on USB Flash Drive. Calibration Sheets: Provide field or factory calibration sheet for each instrument and control device that can be calibrated. Software Code Listing: Providea printout listing and an electronic copy of canned configurable and custom application software for Owner.
809 | 230970 | CONTROL SYSTEMS | 1.9 | WARRANTY | Warranty | The BAS Contractor shall provide (starting at the date the BAS is turned over to the Owner), a one-year warranty and preventative maintenance agreement for the system, as part of the original bid. Any manufacturing defects arising during the warranty period shall be corrected without additional cost to the Owner. The preventative maintenance agreement shall includea minimum of quarterly service visits, include defective parts replacement and commence upon completion of the BAS system installation and acceptance by the Owner. Cost of the preventative maintenance agreement shall be listed asa separate item in the bid response. During the warranty period, the BAS Contractor shall respond to any problem related to the functional operation of the BAS. If BAS has been turned over to the Owner anda site presence has been removed from the project, then an on-line support service may allow the local BAS Contractor to monitor and control the facility's building automation system with Owners prior approval. If the Owner enables the BAS Contractor to have 24/7 remote access to the system via internet connection, then: o Coverage shall include normal business hours, after business hours, weekends and holidays and require response to any problems within two (2) hours of the time that the problem is reported, unless otherwise agreed to with Owner. o If local office cannot resolve the problem on-line, the national office of the building automation system manufacturer shall have the same capabilities for remote connection to the facility. o If the problem cannot be resolved with on-line support services, the BAS contractor shall dispatch the appropriate personnel to the job site to resolve the problem within 24 hours of the time that the problem is reported.
810 | 230970 | CONTROL SYSTEMS | 1.10 | TRAINING | O&M Training And Demonstration | The BAS Contractor shall providea separate cost fora Factory Sanctioned training course to Owners engineers, technicians, and operators. Five days of training will be scheduled as follows; One (1) two-day (2-day) session followed by one-day (1-day) sessions every three (3) months over the course of one (1) year from the date of system turnover to Owner. Contractor shall cover training course costs, travel, and lodging expenses fora Training Course executed at the Owners site. Course shall address system operation and preventative maintenance for the BAS system. Course shall include all materials and training aids necessary for up to 10 students. Cost of this course shall be listed asa separate item in the bid response. Training shall include: 1. Explanation of drawings, operations and maintenance manuals. 2. Walk-through of the job to locate control components. 3. Operator workstation and peripherals. 4. DDC controller and ASC operation/function. 5. Operator control functions including graphic generation and field panel programming. 6. Operation of portable operator's terminal. 7. Explanation of adjustment, calibration and replacement procedures. 8. Student binder with training modules. Since the Owner may require personnel to have more comprehensive understanding of the hardware and software, additional training must be available from the Manufacturer. If the Owner requires such training, it will be contracted ata later date.
814 | 230971 | HVAC SEQUENCE OF CONTROL | 1.3 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - SEQUENCE OF CONTROL................................................................................................................ 1
815 | 230971 | HVAC SEQUENCE OF CONTROL | 1.3 | SUBMITTALS | General | The following sequences shall be augmented as necessary by the Controls contractor and submitted either as part of the controls submittal or asa separate Functional Requirements Specification for approval by the Engineer and Owner prior to commencing any programming.
816 | 230972 | PLANT UTILITIES SEQUENCE OF CONTROL | 1.3 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS NOT APPLICABLE..................................................................................................... 1 PART 3. - SEQUENCE OF CONTROL................................................................................................................ 1
817 | 230972 | PLANT UTILITIES SEQUENCE OF CONTROL | 1.3 | SUBMITTALS | General | The following sequences shall be augmented as necessary by the Controls contractor and submitted either as part of the controls submittal or asa separate functional requirements specification for approval by the Engineer and Owner prior to commencing any programming.
818 | 230990 | TESTING, ADJUSTING, AND BALANCING | 1.4.-1.5 | SUBMITTALS | Samples | Documents Examination Report: Within 20 days of Contractor's Notice to Proceed, submit the Contract Documents review report as specified in Part 3. Strategies and Procedures Plan: Within 30 days of Contractor's Notice to Proceed, submit TAB strategies and step-by-step procedures as specified in "Preparation" Article 3.3. Certified TAB reports upon completion of TAB. Sample report forms prior to commencing TAB. Instrument calibration reports with final report, to include the following: Instrument Type and Make Serial Number Application Dates of Use Dates of Calibration
820 | 230990 | TESTING, ADJUSTING, AND BALANCING | 3.17 | FINAL REPORT | Reports | General: Preparea certified written report; tabulate and divide the report into separate sections for tested systems and balanced systems. Includea certification sheet at the front of the report's binder, signed and sealed by the certified testing and balancing engineer. Includea list of instruments used for procedures, along with proof of calibration. Final Report Contents: In addition to certified field-report data, include the following: Pump curves. Fan curves. Manufacturers' test data. Field test reports prepared by system and equipment installers. Other information relative to equipment performance; do not include Shop Drawings and product data. General Report Data: In addition to form titles and entries, include the following data: Title page. Name and address of the TAB contractor. Project name. Project location. Architect's name and address. Engineer's name and address. Contractor's name and address. Report date. Signature of TAB supervisor who certifies the report. Table of Contents with the total number of pages defined for each section of the report. Number each page in the report. Summary of contents including the following: Indicated versus final performance. Notable characteristics of systems. Description of system operation sequence if it varies from the Contract Documents. Nomenclature sheets for each item of equipment. Data for terminal units, including manufacturer's name, type, size, and fittings. Notes to explain why certain final data in the body of reports vary from indicated values by more than the allowable tolerance. Test conditions for fans and pump performance forms including the following: Settings for outdoor-, return-, and exhaust-air dampers. Conditions of filters. Cooling coil, wet- and dry-bulb conditions. Face and bypass damper settings at coils. Fan drive settings including settings and percentage of maximum pitch diameter. Inlet vane settings of fan speeds for variable-air-volume systems. Settings for supply-air, static-pressure controller. Other system operating conditions that affect performance. System Diagrams: Include schematic layouts of air and hydronic distribution systems. Present each system with single-line diagram and include the following: Quantities of outdoor, supply, return, and exhaust airflows. Water and steam flow rates. Duct, outlet, and inlet sizes. Pipe and valve sizes and locations. Terminal units. Balancing stations. Position of balancing devices. Room Pressurization Test Reports: Data: Door or gap opening identification. Location. Test Data (Actual Values): Relative room pressure in inches wg. Differential pressure across opening in inches wg. Airflow direction through gaps. Air-Handling-Unit Test Reports: For air-handling units with coils, include the following: Unit Data: Unit identification. Location. Make and type. Model number and unit size. Manufacturer's serial number. Unit arrangement and class. Discharge arrangement. Sheave make, size in inches, and bore. Center-to-center dimensions of sheave, and amount of adjustments in inches. Number, make, and size of belts. Number, type, and size of filters. Motor Data: Motor make, and frame type and size. Horsepower and rpm. Volts, phase, and hertz. Full-load amperage and service factor. Sheave make, size in inches, and bore. Center-to-center dimensions of sheave, and amount of adjustments in inches. Test Data (Indicated and Actual Values): Total air flow rate in cfm. Total system static pressure in inches wg. Fan rpm. Discharge static pressure in inches wg. Filter static-pressure differential in inches wg. Preheat-coil static-pressure differential in inches wg. Cooling-coil static-pressure differential in inches wg. Heating-coil static-pressure differential in inches wg. Outdoor airflow in cfm. Return airflow in cfm. Static Pressure Profile Outdoor-air damper position. Return-air damper position. Vortex damper position (if applicable). Apparatus-Coil Test Reports: Coil Data: System identification. Location. Coil type. Number of rows. Fin spacing in fins per inch o.c. Make and model number. Face area in sq. ft. Tube size in NPS. Tube and fin materials. Circuiting arrangement. Test Data (Indicated and Actual Values): Air flow rate in cfm. Average face velocity in fpm. Air pressure drop in inches wg. Outdoor-air, wet- and dry-bulb temperatures in deg F. Return-air, wet- and dry-bulb temperatures in deg F. Entering-air, wet- and dry-bulb temperatures in deg F. Leaving-air, wet- and dry-bulb temperatures in deg F. Water flow rate in gpm. Water pressure differential in feet of head or psig. Entering-water temperature in deg F. Leaving-water temperature in deg F. Refrigerant expansion valve and refrigerant types. Refrigerant suction pressure in psig. Refrigerant suction temperature in deg F. Inlet steam pressure in psig. Fan Test Reports: For supply, return, and exhaust fans, include the following: Fan Data: System identification. Location. Make and type. Model number and size. Manufacturer's serial number. Arrangement and class. Sheave make, size in inches, and bore. Center-to-center dimensions of sheave, and amount of adjustments in inches. Motor Data: Motor make, and frame type and size. Horsepower and rpm. Volts, phase, and hertz. Full-load amperage and service factor. Sheave make, size in inches, and bore. Center-to-center dimensions of sheave, and amount of adjustments in inches. Number, make, and size of belts. Test Data (Indicated and Actual Values): Total airflow rate in cfm. Total system static pressure in inches wg. Fan rpm. Discharge static pressure in inches wg. Suction static pressure in inches wg. Round and Rectangular Duct Traverse Reports: Includea diagram witha grid representing the duct cross-section and record the following: Report Data: System and air-handling-unit number. Location and zone. Traverse air temperature in deg F. Duct static pressure in inches wg. Duct size in inches. Duct area in sq. ft. Indicated air flow rate in cfm. Indicated velocity in fpm. Actual air flow rate in cfm. Actual average velocity in fpm. Barometric pressure in psig. System-Coil Reports: For reheat coils and water coils of terminal units, include the following: Unit Data: System and air-handling-unit identification. Location and zone. Room or riser served. Coil make and size. Flowmeter type. Test Data (Indicated and Actual Values): Air flow rate in cfm. Entering-water temperature in deg F. Leaving-water temperature in deg F. Water pressure drop in feet of head or psig. Entering-air temperature in deg F. Leaving-air temperature in deg F. Pump Test Reports: Calculate impeller size by plotting the shutoff head on pump curves and include the following: Unit Data: Unit identification. Location. Service. Make and size. Model number and serial number. Water flow rate in gpm. Water pressure differential in feet of head or psig. Net positive suction head available in feet of head or psig. Pump rpm. Impeller diameter in inches. Motor make and frame size. Motor horsepower and rpm. Voltage at each connection. Amperage for each phase. Full-load amperage and service factor. Seal type. Test Data (Indicated and Actual Values): Static head in feet of head or psig. Pump shutoff pressure in feet of head or psig. Actual impeller size in inches. Full-open flow rate in gpm. Full-open pressure in feet of head or psig. Final discharge pressure in feet of head or psig. Final suction pressure in feet of head or psig. Final total pressure in feet of head or psig. Final water flow rate in gpm. Voltage at each connection. Amperage for each phase. Instrument Calibration Reports: Report Data: Instrument type and make. Serial number. Application. Dates of use. Dates of calibration.
822 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.6 | WARRANTIES AND GUARANTEES | Warranty | In addition to warranties called for in other sections of these specifications, work shall be guaranteed against defect due to faulty installation, manufacture, and component design. Warranties and guarantees shall be fora period of not less than one year, beginning on the later date of final acceptance by Owners Representative, or equipment start-up. Upon written notice from the Owners Representative or Engineer, promptly remedy, without cost to the Owners Representative, any defects occurring or discovered during the guarantee period.
823 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.7 | SUBMITTALS | General | General Provide submittals of material or equipment in accordance with the Submittal Requirement Schedule at the end of this specification section. A submittal is required if an "X" is indicated for that column and item. Some specification sections have very specific submittal requirements, not indicated in this section, and therefore are indicated in that specific specification section. The Architect/Engineer reserves the right to withhold action on all shop drawing and product data submittals until the Construction Manager deliversa register of anticipated submittals for review and comment. The register must indicate (estimated) issue dates for all future submittals. Submittal dates should be linked to construction milestones factoring in product lead times. The Construction Manager should also indicate schedule impact if submittal response is outside of the allowable review period. The Architect/Engineer reserves the right to delay review of submittals that have no impact or bearing on the construction schedule. Acceptable Manufacturers Subject to compliance with the requirements of the individual specification sections, provide materials and equipment from the indicated manufacturers only. Submittals of material or equipment manufactured by other than those indicated will be returned. 1.7.1. Review Action The Contractor is responsible for all data and information on submittals, including quantities, sizes, dimensions, and compliance with the Drawings and Specifications. Checking by the Owners Representative is only for general conformance with the design concept of the project and general compliance with the information given in the Contract Documents. Any action shown is subject to the requirements of the Drawings and Specifications. Contractor is responsible for dimensions and quantities which shall be confirmed at the jobsite, and fabrication process and techniques of construction. Except for submittals for record, information for similar purposes, where action and return are required or requested, the Owners Representative will check each submittal, mark to indicate action taken, and return promptly. Compliance with specified characteristics is the Contractor's responsibility. 1.7.2. Shop Drawings Submit information, drawn to accurate scale. Highlight, encircle, or otherwise indicate deviations from the Contract Documents. Do not reproduce Contract Documents (unless authorized by the Owners Representative/Engineer) or copy standard information as the basis of Shop Drawings. Standard information prepared without specific reference to the Project are not considered Shop Drawings. Shop Drawings include fabrication and installation drawings, setting diagrams, schedules, patterns, templates and similar drawings, and directions for installation of anchorages. Include asa minimum the following information on drawings or diagrams: Dimensions Identification of products and materials included Compliance with specified standards Notation of coordination requirements Notation of dimensions established by field measurement Clearances for access and service 1.7.3. Product Data Collect Product Data intoa single submittal for each element of construction or system. Where Product Data must be specially prepared because standard printed data is not suitable for use, submit as Shop Drawings. Product Data Information: Includes catalog cuts, sketches, or bulletins indicating performance characteristics, features of equipment, controls, instrumentation, valving, equipment dimensions, materials of construction, estimated weight of unit (shipping, installed, and operating), heat rejection load when operating, auxiliaries, specialties, or accessories furnished, roughing-in or anchor diagrams and templates, manufacturer's installation instructions, service clearance requirements, standard color charts, and wiring diagrams. Schematic Drawings shall include elevation and plan views, and indicate all connections, attachments, and details to indicate field required general details of assembly, etc. Wiring diagrams shall detail wiring for power, signal, and control systems, differentiating between manufacturer- installed wiring and field-installed wiring. Mark each copy to show applicable choices and options. Where printed Product Data includes information on several products, some of which are not required, mark copies to indicate the applicable information. Include the following information with above product data: Manufacturer's printed recommendations Compliance with recognized trade association standards Compliance with recognized testing agency standards Application of testing agency labels and seals Notation of dimensions verified by field measurement Notation of coordination requirements
826 | 260519 | LOW VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES | 1.5 | SUBMITTALS................................................................................................................................... 3 | General | PART 2.- PRODUCTS........................................................................................................................................... 3
828 | 260519 | LOW VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of product.
830 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5 | SUBMITTALS............................................................................................................................ 2 | General | PART 2. - PRODUCTS................................................................................................................................... 3
832 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5.-1 | SUBMITTALS | General | Grounding arrangements and connections for separately derived systems.
834 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5.-1 | SUBMITTALS | O&M Manuals | In addition to items specified in Section 017823 "Operation and Maintenance Data," include instructions for periodic testing and inspection of grounding features at grounding connections for separately derived systemsbased on NETA MTS and NFPA 70B: a. Tests shall determine if ground-resistance or impedance values remain within specified maximums, and instructions shall recommend corrective action if values do not. b. Include recommended testing intervals.
833 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5.-2 | SUBMITTALS | O&M Manuals | Interconnection with building structural and foundation steel. Qualification Data: For testing agency and the testing agency's field supervisor. Field quality control reports. Operation and Maintenance Data: For grounding system components to be included in emergency, operation, and maintenance manuals related to sensitive electronic equipment.
849 | 260533 | RACEWAYS | 1.5 | SUBMITTALS | Product Data | Product Data: For surface raceways, wireways and fittings, floor boxes, hinged-cover enclosures, and cabinets.
851 | 260534 | ELECTRICAL BOXES AND FITTINGS | 1.4 | SUBMITTAL REQUIREMENTS | Product Data | Product Data: For each type of product including but not limited to materials, finishes, separators and miscellaneous components.
855 | 260548 | VIBRATION AND SEISMIC CONTROLS FOR ELECTRICAL SYST | 1.5 | SUBMITTALS | General | Refer to Section 260500 Basic Electrical Requirements. Product Data: Submit complete seismic calculations and restraint device shop drawings for review to the engineer. These calculations shall be stamped bya Contractor-hired registered seismic restraint engineer. Submittals shall be coordinated with building structural engineer and shall include: Certification in writing that installation has been inspected by Engineer at completion of mechanical rough-in and is in compliance with reference standards and accepted practices. Product Data: For each type of product. Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of seismic-restraint component used. o Tabulate types and sizes of seismic restraints. o Annotate to indicate application of each product submitted and compliance with requirements. Delegated-Design Submittal: For each seismic restraint device. Include design calculations and details for selecting seismic restraints complying with performance requirements, design criteria, and analysis data signed and sealed by the qualified professional engineer responsible for their preparation. Design Calculations: Calculate static and dynamic loading caused by equipment weight, operation, and seismic forces required to select seismic restraints and for designing vibration isolation bases. Coordinate design calculations with wind load calculations required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors. Calculations, drawings and details showing methods for suspension, support, guides, and attachment to structure for all cable tray, conduit rack, lights, and equipment. Seismic Restraint Details: Design Analysis: To support selection and arrangement of seismic restraints. Include calculations of combined tensile and shear loads. Details: Indicate fabrication and arrangement. Detail attachments of restraints to the restrained items and to the structure. Show attachment locations, methods, and spacings. Identify components, list their strengths, and indicate directions and values of forces transmitted to the structure during seismic events. Indicate association with vibration isolation devices. Coordinate seismic-restraint and vibration isolation details with wind-restraint details required for equipment mounted outdoors. Comply with requirements in other Sections for equipment mounted outdoors. Drawings showing methods for suspension, support, guides, etc., for all electrical systems. Drawings showing methods for isolation and seismic restraint of feeders, etc., piercing walls, etc. Cable tray and conduit rack routing supports and braces shall be actual and specific to this project. Typical catalog cuts and details will not be accepted. Drawings and details showing methods for isolation with seismic restraint of cable tray, conduit rack, lights, etc. Field quality-control reports.
853 | 260548 | VIBRATION AND SEISMIC CONTROLS FOR ELECTRICAL SYST | 1.7 | WARRANTY..................................................................................................................................... 3 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 3
856 | 260548 | VIBRATION AND SEISMIC CONTROLS FOR ELECTRICAL SYST | 1.7 | WARRANTY | Manufacturers Warranty | Manufacturers Warranty: Manufacturers warranties shall not be violated by installation of seismic restraint and/or support devices and equipment.
858 | 260573 | POWER SYSTEMS STUDIES E | 1.5 | SUBMITTALS................................................................................................................................... 3 | General | PART 2. - PRODUCTS.......................................................................................................................................... 4
863 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-A | SUBMITTALS | Product Data | Product Data : For computer software program to be used for studies.
864 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-B | SUBMITTALS | Reports | Submit the following after the approval of system protective devices submittals. Submittals shall be in digital form. i) Provide two (2) bound copies of the completed analysis to the Construction Manager, Architect/ Engineer. ii) The Contractor must be prepared to submit at least (4) iterations of the combined study report. This includes an initial report; up to (2) revised reports at no additional cost to the Owner to incorporate design revisions, field changes and address comments by the Engineer; anda final report for record. Each re-submittal must include formal typewritten responses to comments by the Engineer.
865 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-C | SUBMITTALS | Reports | Short-circuit study input data, including completed computer program input data sheets. i) Short-circuit study and equipment evaluation report; signed, dated, and sealed bya qualified professional engineer licensed in the state where the project is taking place. ii) Submit study report for action prior to receiving final approval of the distribution equipment submittals. If formal completion of studies will cause delay in equipment manufacturing, obtain approval from Engineer for preliminary submittal of sufficient study data to ensure that the selection of devices and associated characteristics is satisfactory. iii) Includea one-line diagram on Drawings asa scope document for the short-circuit study. iv) Revised single-line diagram, reflecting field investigation results and results of short-circuit study. v) A computer-based, feeder and branch circuit load flow and voltage drop study to determine voltage levels at distribution equipment under ordinary load flow conditions. vi) Coordination-study input data, including completed computer program input data sheets. vii) Electronic model and database used to perform studies. viii) Study and equipment evaluation reports.
866 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-D | SUBMITTALS | Reports | Overcurrent protective device coordination study report : signed, dated, and sealed bya qualified professional engineer licensed in the state where the project is taking place. i) Submit study report for action prior to receiving final approval of the distribution equipment submittals. If formal completion of studies will cause delay in equipment manufacturing, obtain approval from Engineer for preliminary submittal of sufficient study data to ensure that the selection of devices and associated characteristics is satisfactory.
867 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-E | SUBMITTALS | Reports | Arc-flash study input data, including completed computer program input data sheets licensed in the state where the project is taking place. i) Arc-flash study report; signed, dated, and sealed bya qualified professional engineer. (1) Submit study report for action prior to receiving final approval of the distribution equipment submittals. If formal completion of studies will cause delay in equipment manufacturing, obtain approval from Architect for preliminary submittal of sufficient study data to ensure that the selection of devices and associated characteristics is satisfactory. (2) Arc-flash hazard warning labels
868 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-F | SUBMITTALS | Qualification Data | Qualification Data : For Study Software Developer as required by the Quality Assurance Article. i) Product Certificates: For study software, certifying compliance with IEEE 399 for short-circuit and device coordination analysis; certifying compliance with IEEE 1584 and NFPA 70E for arc-flash hazard analysis.
869 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-G | SUBMITTALS | O&M Manuals | Closeout submittals i) Operation and Maintenance Data: For the overcurrent protective devices to include in emergency, operation, and maintenance manuals. ii) In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following: iii) The following parts from the Protective Device Coordination Study Report: iv) One-line diagram. v) Protective device coordination study. vi) Time-current coordination curves. vii) Power system data viii) All necessary electronic files, in their native formats, used to perform the power system studies.
870 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-H | SUBMITTALS | General | Maintenance procedures according to requirements in NFPA 70E shall be provided in the equipment manuals.
871 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-I | SUBMITTALS | O&M Manuals | Operation and Maintenance Procedures : provide maintenance procedures for use by Owner's personnel that comply with requirements in NFPA 70E.
872 | 260573 | POWER SYSTEMS STUDIES E | 1.5.-J | SUBMITTALS | Reports | Power factor correction study report
873 | 260573 | POWER SYSTEMS STUDIES E | 3.1.-B | EXAMINATION AND POWER SYSTEM DATA | Product Data | Gather and tabulate the following input data to support the initial short-circuit and subsequent studies. Comply with recommendations in IEEE 551 as to the amount of detail that is required to be acquired in the field. Field data gathering shall be under the direct supervision and control of the engineer in charge of performing the study and shall be by the engineer or its representative who holds NETA ETT Level III certification or NICET Electrical Power Testing Level III certification. a. Product Data for overcurrent protective devices specified in other Sections and involved in overcurrent protective device coordination studies. Use equipment designation tags that are consistent with electrical distribution system diagrams, overcurrent protective device submittals, input and output data, and recommended device settings. b. Electrical power utility impedance at the service. c. Power sources and ties. d. Short-circuit current at each system bus, three phase and line-to-ground. e. Full-load current of all loads. f. Voltage level at each bus. g. For transformers, include kVA, primary and secondary voltages, connection type, impedance, X/R ratio, taps measured in percent, and phase shift. h. For reactors, provide manufacturer and model designation, voltage rating, and impedance. i. For circuit breakers and fuses, provide manufacturer and model designation. List type of breaker, type of trip and available range of settings, SCCR, current rating, and breaker settings. j. For relays, provide manufacturer and model designation, current transformer ratios, potential transformer ratios, and relay settings. k. Maximum demands from service meters. l. Busway manufacturer and model designation, current rating, impedance, lengths, and conductor material. m. Motor horsepower and NEMA MG 1 code letter designation. n. Low-voltage cable sizes, lengths, number, conductor material, and conduit material (magnetic or nonmagnetic). o. Medium-voltage cable sizes, lengths, conductor material, and cable construction and metallic shield performance parameters. p. Data sheets to supplement electrical distribution system diagram, cross-referenced with tag numbers on diagram, showing the following: i. Special load considerations, including starting inrush currents and frequent starting and stopping. ii. Transformer characteristics, including primary protective device, magnetic inrush current, and overload capability. iii. Motor full-load current, locked rotor current, service factor, starting time, type of start, and thermal-damage curve. iv. Ratings, types, and settings of utility company's overcurrent protective devices. v. Special overcurrent protective device settings or types stipulated by utility company. vi. Time-current-characteristic curves of devices indicated to be coordinated. vii. Manufacturer, frame size, interrupting rating in amperes rms symmetrical, ampere or current sensor rating, long-time adjustment range, short-time adjustment range, and instantaneous adjustment range for circuit breakers. viii. Manufacturer and type, ampere-tap adjustment range, time-delay adjustment range, instantaneous attachment adjustment range, and current transformer ratio for overcurrent relays. ix. Panelboards, switchboards, motor-control center ampacity, and SCCR in amperes rms symmetrical. x. Identify series-rated interrupting devices fora condition where the available fault current is greater than the interrupting rating of the downstream equipment. Obtain device data details to allow verification that series application of these devices complies with NFPA 70 and UL 489 requirements.
876 | 260923 | LIGHTING CONTROL DEVICES | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of product Shop Drawings: Show installation details for occupancy and light-level sensors, interconnection diagrams showing field-installed wiring, and diagrams for power, signal, and control wiring. Operation and Maintenance Data: For each type of product to include in emergency, operation, and maintenance manuals. Field quality-control test reports. California Energy Commission Certificates of Installation and Certificates of Acceptance, in accordance with the California Building Energy Efficiency Standards. Agreement to Maintain: Prior to time of final acceptance, the Contractor shall submit four (4) copies of an agreement for continued service and maintenance of lighting control equipment, for Owner's possible acceptance. Offer terms and conditions for furnishing parts and providing continued testing and servicing, including replacement of materials and equipment, for one-year period with option for renewal of Agreement by the Owner.
874 | 260923 | LIGHTING CONTROL DEVICES | 1.6 | WARRANTY..................................................................................................................................... 2 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 2
877 | 260923 | LIGHTING CONTROL DEVICES | 1.6 | WARRANTY | Warranty | The manufacturer shall warrant all equipment and systems provided under this section to be free from defects in materials and workmanship fora period of at least one year from the date of completion of all work in this section.
882 | 260923 | LIGHTING CONTROL DEVICES | 3.6 | TRAINING AND DEMONSTRATION | O&M Training And Demonstration | Train Owners maintenance personnel to adjust, operate, and maintain lighting control devices. Demonstrate operation of the products specified in this section.
885 | 262200 | LOW VOLTAGE TRANSFORMERS | 1.5 | SUBMITTALS | Product Data | Product Data: Submit manufacturer's technical product data including rated KVA, frequency, primary and secondary voltages, percent taps, percent impedance, and certification of transformer performance efficiency at indicated full loads, percentage regulation at 100% and 80% power factor, no-load and full-load losses in watts, average temperature rise above ambient temperature, sound level in decibels, and standard published data. Shop Drawings: For each transformer and related equipment, include: Dimensioned plans, elevations, sections, and details. Show tabulations of installed devices, equipment features, and ratings. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. Detail bus configuration, current, and voltage ratings. Detail features, characteristics, ratings, and factory settings of individual auxiliary components. Include power wiring diagrams indicating tap connections available. Qualification Data: For qualified testing agency. Seismic Qualification Certificates: Submit certification that transformers, accessories, and components will withstand seismic forces defined in Division 26 Section Vibration and Seismic Controls for Electrical Systems. Include the following: Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation. Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For transformers include maintenance manuals.
883 | 262200 | LOW VOLTAGE TRANSFORMERS | 1.8 | WARRANTY..................................................................................................................................... 4 | Warranty | PART 2.- PRODUCTS........................................................................................................................................... 4
886 | 262200 | LOW VOLTAGE TRANSFORMERS | 1.8-1 | WARRANTY | Warranty | Warranty Period : 18 months minimum
891 | 262416 | PANELBOARDS | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of panelboard, switching and overcurrent protective device, surge protection device, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: For each panelboard and related equipment, include: Dimensioned plans, elevations, sections, and details. Show tabulations of installed equipment features, and ratings. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. Detail bus configuration, current, and voltage ratings. Qualification Data: For qualified testing agency. Seismic Qualification Certificates: Submit certification that transformer will withstand seismic forces defined in Division 26 Section Vibration and Seismic Controls for Electrical Systems. Include the following: Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation. Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Panelboard Schedules: For installation in panelboards. Operation and Maintenance Data: For panelboards and components to include in emergency, operation, and maintenance manuals.
892 | 262416 | PANELBOARDS | 1.7 | EXTRA MATERIALS | Attic Stock | Provide pint of touch up paint for every ten (10) panelboards installed. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. Keys: Two (2) spares for each type of panelboard cabinet lock.
889 | 262416 | PANELBOARDS | 1.9 | WARRANTY..................................................................................................................................... 4 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 4
893 | 262416 | PANELBOARDS | 1.9.-1 | WARRANTY | Warranty | Warranty Period : 18 months minimum Special Warranty: Manufacturers standard form in which manufacturer agrees to repair or replace surge protection devices that fail in materials or workmanship within specified warranty period.
894 | 262416 | PANELBOARDS | 1.9.-1 | WARRANTY | Warranty | Warranty Period : 10 years minimum
899 | 262419 | MOTOR CONTROL CENTERS | 1.5 | SUBMITTAL REQUIREMENTS | Product Data | Product Data: For each type of motor control center, accessory, and component indicated. Include dimensioned elevations, sections, weights, material descriptions and manufacturers' technical data on features, performance, electrical characteristics, ratings, accessories, and finishes. Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories for each cell of the MCC. 1. Enclosure types and details for all types 2. Current and voltage ratings. 3. Short-circuit current ratings (interrupting and withstand, as appropriate). 4. Include evidence of NRTL listing for full rating of installed devices. 5. Detail features, characteristics, ratings, and factory settings of individual overcurrent protective devices and motor circuit protectors, accessories, and auxiliary components. 6. Include time-current coordination curves for each type and rating of overcurrent protective devices and motor circuit protectors; include selectable ranges for each type of overcurrent protective device. Shop Drawings: For each MCC, manufacturer's drawings as defined in UL 845. In addition to requirements specified in UL 845, include dimensioned plans, elevations, and sections; and conduit entry locations and sizes, mounting arrangements, and details, including required clearances and service space around equipment. 1. Show tabulations of installed devices, equipment features, and ratings. Include the following: a. Each installed unit's type and details. b. Bus Configuration, current, and voltage ratings c. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. d. Dimensioned plans, elevations, sections, and details. Show tabulations of installed devices, equipment features, and ratings. e. Include evidence of NRTL listing for series rating of installed devise. f. Include evidence of NRTL listing for SPD as installed in motor control center. g. Factory-installed devices. h. Enclosure types and details. i. Nameplate legends. j. Short-circuit current (withstand) rating of complete MCC, and for bus structure and each unit. k. Features, characteristics, ratings, and factory settings of each installed controller and feeder device, and installed devices. l. Specified optional features and accessories. 2. Schematic and Connection Wiring Diagrams: For power, signal, and control wiring for each installed controller. 3. Nameplate legends. 4. Vertical and horizontal bus capacities. 5. Features, characteristics, ratings, and factory settings of each installed unit. Qualification Data: For qualified testing agency. Seismic Qualification Certificates: Submit certification that motor control center, overcurrent protective devices, accessories, and components will withstand seismic forces defined in Division 26 Section Vibration and Seismic Controls for Electrical Systems. Include the following: Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation. Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements. Field Quality-Control Reports 1. Test procedures used. 2. Test results that comply with requirements. 3. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For enclosed circuit breakers to include in emergency, operation, and maintenance manuals. In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following: 1. Manufacturer's written instructions for testing and adjusting enclosed circuit breakers. 2. Time-current coordination curves for each type and rating of overcurrent protective device; include selectable ranges for each type of overcurrent protective device.
900 | 262419 | MOTOR CONTROL CENTERS | 1.7 | EXTRA MATERIALS | Attic Stock | Maintenance Stock, Fuses: For types and ratings required, furnish additional fuses, amounting to one (1) unit for every 10 installed units, but not less than three (3) units of each. This includes but is not limited to, potential transformer fuses, control power fuses, fusible circuit breakers, fused switches, and fused power circuit devices. Provide spare LEDs not less than six (6) of each type installed. Provide pint of touch-up paint.
897 | 262419 | MOTOR CONTROL CENTERS | 1.9 | WARRANTY..................................................................................................................................... 5 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 5
901 | 262419 | MOTOR CONTROL CENTERS | 1.9-1 | WARRANTY | Warranty | Warranty Period : 18 months minimum Special Warranty: Manufacturers standard form in which manufacturer agrees to repair or surge protection devices that fail in materials or workmanship within specified warranty period.
902 | 262419 | MOTOR CONTROL CENTERS | 1.9-1 | WARRANTY | Warranty | Warranty Period : 10 years minimum
905 | 262419 | MOTOR CONTROL CENTERS | 3.8 | DEMONSTRATION | O&M Training And Demonstration | Subsequent to wire and cable hook-ups, energize switchboards and test functioning for compliance with requirements. Where necessary, correct malfunctioning units, and then retest for compliance.
906 | 262419 | MOTOR CONTROL CENTERS | 3.9 | REPORTS | Reports | After energizing switchboard, submit copies of reports for all tests indicated above for review by the Engineer.
907 | 262726 | WIRING DEVICES | 1.5 | SUBMITTALS................................................................................................................................... 2 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
909 | 262726 | WIRING DEVICES | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of product. Closeout submittals: Operation and Maintenance Data: For wiring devices to include in all manufacturers' packing-label warnings and instruction manuals that include labeling conditions.
913 | 262816 | ENCLOSED SWITCHES AND CIRCUIT BREAKERS | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of enclosure, switching and overcurrent protective device, surge protection device, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: For each enclosure and related equipment, include: Dimensioned plans, elevations, sections, and details. Show tabulations of installed equipment features, and ratings. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. Detail bus configuration, current, and voltage ratings. Qualification Data: For qualified testing agency. Seismic Qualification Certificates: Submit certification that switch, and circuit breaker enclosures will withstand seismic forces defined in Division 26 Section Vibration and Seismic Controls for Electrical Systems. Include the following: Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation. Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For equipment and components to include in emergency, operation, and maintenance manuals.
914 | 262816 | ENCLOSED SWITCHES AND CIRCUIT BREAKERS | 1.7 | EXTRA MATERIALS | Attic Stock | Provide pint of touch up paint for every twenty-five (25) enclosures installed, but not less than pint of touch up paint. Furnish extra materials as indicated in related specification documents.
911 | 262816 | ENCLOSED SWITCHES AND CIRCUIT BREAKERS | 1.9 | WARRANTY..................................................................................................................................... 3 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 4
915 | 262816 | ENCLOSED SWITCHES AND CIRCUIT BREAKERS | 1.9.-1 | WARRANTY | Warranty | Warranty Period : 18 months minimum
917 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.8 | WARRANTY..................................................................................................................................... 4 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 4
919 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-1 | SUBMITTAL REQUIREMENTS | General | Show tabulations of each variable frequency controller. Include the following : - i. Type of enclosure. ii. Equipment weight. iii. Input power supply requirements (volts/phase/amps). iv. Output power characteristics. v. HP range of motors drive is capable of driving. vi. Short-circuit current rating (SCCR) of assembly. vii. Converter pulse rate. viii. Network communications I/O interface capabilities. ix. Specified filters.
921 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-1 | SUBMITTAL REQUIREMENTS | Certifications | Basis for Certification : Indicate whether withstand certification is based on actual test of assembled components or on calculation.
924 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-1 | SUBMITTAL REQUIREMENTS | General | Test procedures used.
927 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-1 | SUBMITTAL REQUIREMENTS | General | A complete listing of all programming parameters.
920 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-2 | SUBMITTAL REQUIREMENTS | Wiring Diagram | Schematic and Connection Wiring Diagrams : For power, signal, and control wiring for each installed variable frequency controller. Qualification Data: For qualified testing agency. Seismic Qualification Certificates: Submit certification that variable frequency controller, overcurrent protective devices, accessories, and components will withstand seismic forces defined in Division 26 Section Vibration and Seismic Controls for Electrical Systems. Include the following:
922 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-2 | SUBMITTAL REQUIREMENTS | Drawings | Dimensioned Outline Drawings of Equipment Unit : Identify center of gravity and locate and describe mounting and anchorage provisions.
925 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-2 | SUBMITTAL REQUIREMENTS | General | Test results that comply with requirements.
928 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-2 | SUBMITTAL REQUIREMENTS | General | Instructions on how to modify program settings, and modify the control program.
923 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-3 | SUBMITTAL REQUIREMENTS | Reports | Detailed description of equipment anchorage devices on which the certification is based and their installation requirements. Field Quality-Control Reports
926 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-3 | SUBMITTAL REQUIREMENTS | O&M Manuals | Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For each type of variable frequency controller include operation and maintenance manual. In addition to items specified in Division 01 Section "Operation and Maintenance Data", include the following:
929 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-3 | SUBMITTAL REQUIREMENTS | General | Instructions on drive adjustment, trouble-shooting, and configuration.
930 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-4 | SUBMITTAL REQUIREMENTS | General | Instructions on process tuning and system calibration.
931 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-5 | SUBMITTAL REQUIREMENTS | General | Routine maintenance requirements for variable frequency controller and all related components.
932 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-6 | SUBMITTAL REQUIREMENTS | Warranty | Instructions on shutdown procedures and any special instructions for maintaining the warranty.
933 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.5.-7 | SUBMITTAL REQUIREMENTS | General | Instructions on bypass operation.
934 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 1.8-1 | WARRANTY | Warranty | Warranty Period : 12 months minimum, non-prorated warranty on all parts and labor. Warranty period shall begin on the date of project substantial completion or date the drives are put into service by factory trained personnel required for startup and accepted by the Buyer, whichever occurs later.
936 | 262923 | VARIABLE FREQUENCY CONTROLLERS | 3.9 | DEMONSTRATION | O&M Training And Demonstration | Subsequent to wire and cable hook-ups, energize VFDs and test functioning for compliance with project requirements. Where necessary, correct malfunctioning units, and then retest for compliance.
937 | 265113 | INTERIOR LUMINAIRES | 1.7 | WARRANTY..................................................................................................................................... 4 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 4
938 | 265113 | INTERIOR LUMINAIRES | 1.4.-1 | SUBMITTALS | General | Physical description of lighting fixture including dimensions and housing material.
946 | 265113 | INTERIOR LUMINAIRES | 1.4.-1 | SUBMITTALS | Product Data | Requirements indicated above under Product Data.
947 | 265113 | INTERIOR LUMINAIRES | 1.4.-2 | SUBMITTALS | General | Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and locations and size of each field connection.
940 | 265113 | INTERIOR LUMINAIRES | 1.4.-3 | SUBMITTALS | General | Energy-efficiency data for lamps and luminaire efficiency.
948 | 265113 | INTERIOR LUMINAIRES | 1.4.-3 | SUBMITTALS | O&M Manuals | Provide separate shop drawing for each assembly configuration. Fixture assemblies include pendant, cove, track or recessed fixtures with continuous runs that are assembled on site. a. For each continuous row submit detailed drawings of linear and suspended luminaires including dimensions, support spacing, suspension type, power feed type and locations, lamp combinations, driver locations, luminaire joint locations and end plates. b. Detailed drawings for each cove and linear wall system configuration including dimensions, power feed locations, driver locations, luminaire joint locations, extension plates for end and corner sections and end plates. c. For strip luminaires mounted in architectural coves, provide dimensioned drawings and sections and including louver/lens cut sheet. Installation Instructions: Include one set for each fixture type that includes installation instructions for all parts and accessories. Warranty: Provide complete manufacturers warranty information on all products provided. Operation and Maintenance Data: For lighting equipment and fixtures to include in emergency, operation, and maintenance manuals.
941 | 265113 | INTERIOR LUMINAIRES | 1.4.-4 | SUBMITTALS | General | Lamp life mean output lumens, color temperature, and color rendering index.
942 | 265113 | INTERIOR LUMINAIRES | 1.4.-5 | SUBMITTALS | Calculations | Photometric data and adjustment factors based on laboratory tests, complying with IESNA Lighting Measurements Testing & Calculation Guides, of each lighting fixture type. The adjustment factors shall be for lamps, ballasts, and accessories identical to those indicated for the lighting fixture as applied in this Project. a. Manufacturer Certified Data: Photometric data shall be certified bya manufacturers laboratory witha current accreditation under the National Voluntary Laboratory Accreditation Program for Energy Efficient Lighting Products.
943 | 265113 | INTERIOR LUMINAIRES | 1.4.-6 | SUBMITTALS | Wiring Diagram | Wiring diagrams for LED luminaires and compatible drivers indicating remote distances and circuit configuration requirements.
944 | 265113 | INTERIOR LUMINAIRES | 1.4.-7 | SUBMITTALS | General | Control devices or sensors installed integral to luminaires.
945 | 265113 | INTERIOR LUMINAIRES | 1.4.-8 | SUBMITTALS | Shop Drawings | LED submittal requirements provide the following information in addition to the other required preceding information for all LED luminaires: a. Rated input power (in W) b. Rated luminous flux (in lm) c. LED luminaire efficacy (in lm/W) d. Luminous intensity distribution e. Photometric data and adjustment factors based on laboratory tests, complying with IESNA lighting measurements, testing, and calculation guides IES LM-79 [and IES LM-80], for each lighting fixture type. The adjustment factors shall be for lamps and accessories identical to those indicated for the lighting fixture as applied in this Project. f. Photometric code i. Correlated Color Temperature (CCT in K) ii. Rated Color Rendering Index (CRI) iii. Rated chromaticity co-ordinate values (initial and maintained) iv. Maintained luminous flux g. Rated life (in h) of the LED module and the associated rated lumen maintenance (Lx) h. Failure fraction (Fy), corresponding to the rated life of the LED module in the luminaire i. Ambient temperature (ta) fora luminaire j. Power Factor k. Intensity Distribution l. Drive Current m. Dimming Range Shop Drawings: For fixture assemblies, nonstandard, or custom lighting fixtures include details. Include plans, elevations, sections, details, dimensions, weights, components, features, and accessories and the following:
950 | 265113 | INTERIOR LUMINAIRES | 1.7.-1 | WARRANTY | Warranty | Warranty Period for Emergency Lighting Unit Batteries : 10 years from date of Substantial Completion. Full warranty shall apply for first year, and prorated warranty for the remaining nine years.
952 | 265113 | INTERIOR LUMINAIRES | 1.7.-1 | WARRANTY | Warranty | Warranty Period for LED Luminaires : 5 years from date of Substantial Completion. Full warranty shall apply to full term for all parts and accessories, including remote drivers and controllers.
951 | 265113 | INTERIOR LUMINAIRES | 1.7.-2 | WARRANTY | Warranty | Warranty Period for LED Emergency Driver and Self-Powered Exit Sign Batteries : Seven years from date of Substantial Completion. Full warranty shall apply for first year, and prorated warranty for the remaining six years. Warranty for LED Luminaires: Utilize manufacturer's standard form in which manufacturer of LED Luminaire agrees to repair or replace components that fail in materials or workmanship within specified warranty period.
954 | 265113 | INTERIOR LUMINAIRES | 3.7 | TRAINING AND DEMONSTRATION | O&M Training And Demonstration | Demonstrate operation of luminaires with the Owner and the Engineer. Re-aim luminaires as directed by Architect and Engineer.
958 | 312302 | EXCAVATION AND FILL FOR UTILITIES | 1.04-B | SUBMITTALS | Calculations | Drawings and engineering design calculations : Signed and sealed engineering drawings and calculations for required shoring, sheeting, or cribbing for approval prior to starting installation of shoring, sheeting, or cribbing.
961 | 312500 | EROSION AND SEDIMENTATION CONTROLS | 1.05-B | SUBMITTALS | Shop Drawings | Shop drawings : Plans and details, including layout and locations of erosion and sedimentation control features. Indicate dimensions, materials, and anchorage underlying substrates.
962 | 312500 | EROSION AND SEDIMENTATION CONTROLS | 1.05-C | SUBMITTALS | Product Data | Product data : - 1. Manufacturer's detailed technical materials and application data. 2. Submit filter fabric material specifications and installation configuration prior to start of construction.
964 | 321700 | PAVEMENT MARKINGS AND BUMPERS | 1.04-B | SUBMITTALS | Samples | Samples : Minimum 4 inches by 12 inches of pavement marking tape.
965 | 321700 | PAVEMENT MARKINGS AND BUMPERS | 1.04-C | SUBMITTALS | Shop Drawings | Shop drawings : Scaled plan drawings of pavement marking layouts for approval prior to pavement marking application; include alphanumeric sequential identification, as indicated on Drawings or as directed by Owner, on pavement parking spaces and/or precast wheel bumpers.
966 | 321700 | PAVEMENT MARKINGS AND BUMPERS | 1.04-D | SUBMITTALS | Product Data | Product data : Manufacturer's detailed technical materials and application data, including technical bulletins, guides, and manuals, as applicable to the work of this Project, for the following. 1. Pavement marking tape. 2. Pavement marking paint. 3. Reflective glass beads.
970 | 333020 | PROCESS WASTE SYSTEM | 1.04-B | SUBMITTALS | Product Data | Product data : Manufacturer's detailed technical materials, fabrication, and installation data, including technical bulletins, drawings, guides, and manuals, as applicable to the work of this Project.
971 | 333020 | PROCESS WASTE SYSTEM | 1.04-C | SUBMITTALS | Certifications | Certifications : Manufacturer's certification that pipe and fittings have been inspected and tested at the point of origin and are in compliance with specified requirements.
974 | 409010 | BASIC INSTRUMENTATION AND CONTROL REQUIREMENTS | 1.7 | WARRANTIES AND GUARANTEES | Warranty | In addition to warranties called for in other sections of these specifications, work shall be guaranteed against defect due to faulty installation. Warranties and guarantees shall be fora period of not less than one year, beginning on the later date of final acceptance by Owner, or equipment start-up. Upon written notice from the Owner or Owners Representative, promptly remedy, without cost to the Owner, any defects occurring or discovered during the guarantee period.
975 | 409010 | BASIC INSTRUMENTATION AND CONTROL REQUIREMENTS | 1.8 | SUBMITTALS | General | General Provide submittals of material or equipment in accordance with the Submittal Requirement Schedule at the end of this specification section. Some sections have very specific submittals, not indicated in this section, and therefore are indicated ina specific specification section. Additional submittals are required if an "X" is indicated for that column and item. Acceptable Manufacturers Subject to compliance with the requirements of the individual specification sections, provide materials and equipment from the indicated manufacturers only. Submittals of material or equipment manufactured by other than those indicated may be returned. Procedures Coordination: Coordinate preparation and processing of submittals with performance of construction activities. Transmit each submittal sufficiently in advance of performance of related construction activities to avoid schedule delays. Coordinate each submittal with fabrication, purchasing, testing, delivery, other submittals, and related activities that requires sequential activity. Coordinate transmittal of different types of submittals for related elements of the work so processing will not be delayed by the need to review submittals concurrently for coordination. The Owner or Owner's Representative reserves the right to withhold action ona submittal requiring coordination with other submittals until related submittals are received. Processing: Allow sufficient review time so that installation will not be delayed asa result of the time required to process submittals, including time to resubmit. Allow two weeks for initial review. Allow additional time if processing must be delayed to permit coordination with subsequent submittals. The Owner or Owner's Representative will promptly advise the Contractor whena submittal being processed must be delayed for coordination. If an intermediate submittal is necessary, process the same as the initial submittal. Allow two weeks for reprocessing each submittal. No extension of contract time will be authorized because of failure to transmit submittals to the Owner or Owner's Representative sufficiently in advance of the work to permit processing. Preparation: Placea permanent label or title block on each submittal for identification. Indicate the name of the entity that prepared each submittal on the label or title block. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Contractor's review and approval markings and the action taken. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Owner's or Owner's Representative review and approval markings and the action taken. Include the following information on the label or title block for processing and recording action taken. Project name Date Name and address of Owner Name and address of Engineer Name and address of Contractor Name and address of subcontractor Name and address of supplier Name of manufacturer Number and title of appropriate Specification Section Drawing number and detail references, as appropriate Transmittal: Package each submittal appropriately for transmittal and handling. Transmit each submittal from Contractor to Owner or Owner's Representative usinga transmittal form. Submittals received from sources other than the Contractor will be returned without action. Quantity: Submit electronic Portable Document Format (PDF) of each required submittal. The Owner will mark and return electronic copy with action taken and corrections or modifications required. Submittals shall be printed to.pdf, not printed as hard copy and scanned to.pdf. Annotations to.pdf to clarify information, such as indicating specific options on an instrument cut sheet, should be done using editing tools in Adobe, Bluebeam, or comparable program, not hand-marked and scanned. The Engineer or Owner reserves the right to reject submittals without review if the.pdf is not readable or if pixelation occurs on zooming in, rendering enlarged content unreadable. Schedules: Project schedules indicating proposed work phases and sequences. Include in schedule asa minimum, approvals, equipment release, delivery, fabrication, equipment setting, startup, punch, and cleanup. Prepare and submita complete schedule of submittals. Coordinate the submittal schedule with the Contractor's construction schedule. Prepare the schedule in chronological order. Provide the following information: Scheduled date for the submittal Related Section number Submittal category Name of subcontractor Description of the part of the work covered Scheduled date for resubmit Anticipated date for Engineer's final release or approval Distribution: Following response to initial submittal, print and distribute copies to subcontractors and other parties required to comply with submittal requirements. When revisions are made, distribute to the same parties. Delete parties from distribution when they have completed their assigned portion of the work and are no longer involved in construction activities. Updating: Revise the schedule after each meeting or activity, where revisions have been recognized or made. Issue the updated schedule to all parties involved. 1.8.1. Review Action The Contractor is responsible for all data and information on submittals, including quantities, sizes, dimensions, and compliance with the Drawings and Specifications. Checking by the Owner or Owner's Representative is only for general conformance with the design concept of the project and general compliance with the information given in the Contract Documents. Any action shown is subject to the requirements of the Drawings and Specifications. Contractor is responsible for dimensions and quantities that shall be confirmed at the jobsite, and the fabrication process and techniques of construction. 1.8.2. Shop Drawings Submit information, drawn to accurate scale. Highlight, encircle, or otherwise indicate deviations from the Contract Documents. Do not reproduce Contract Documents or copy standard information as the basis of Shop Drawings. Standard information prepared without specific reference to the Project is not considered Shop Drawings. Shop Drawings include fabrication and installation drawings, setting diagrams, schedules, patterns, templates, and similar drawings. Include asa minimum the following information on drawings or diagrams: Dimensions Identification of products and materials included Compliance with specified standards Notation of coordination requirements Notation of dimensions established by field measurement if applicable Clearances for access and service 1.8.3. Product Data Collect Product Data intoa single submittal for each element of construction or system. Where Product Data must be specially prepared because standard printed data is not suitable for use, submit as Shop Drawings. Product Data Information: includes catalog cuts, sketches, or bulletins indicating performance characteristics, features of equipment, controls, instrumentation, equipment dimensions, materials of construction, estimated weights, heat rejection load when operating, auxiliaries, specialties, or accessories furnished, roughing-in or anchor diagrams and templates, manufacturer's installation instructions, service clearance requirements, standard color charts, and wiring diagrams. Mark each copy to show applicable choices and options. Where printed Product Data includes information on several products, some of which are not required, mark copies to indicate the applicable information. Include the following information with above product data: Manufacturer's printed recommendations Compliance with recognized trade association standards Compliance with recognized testing agency standards Application of testing agency labels and seals Notation of dimensions verified by field measurement Notation of coordination requirements Do not submit Product Data until compliance with requirements of the Contract Documents has been confirmed. Instrument Product Data and Format: shall meet the following guidelines: 1. Cover sheet for each submittal, identifying the name of the client, name of the project, Vendors submittal ID, Vendors contact information, date, and purchase order number. 2. Submittals shall include the whole instrument assembly, for example, elements and transmitters, or valves, actuators and position switches. Multiple unrelated instrument types shall not be provided in the same document. 3. Instruments will be grouped by model number and will not contain more than one model number ina grouping. 4. A table for each group will contain the following fields ata minimum, tag number, P&ID, and any other optional important information such as line size, line specification, failure position, wetted elastomers, description, surface finish, etc. This table shall be sorted by Tag Number. 5. A model number code schedule that identifies each character in the model number and describes what the character represents, ora copy of the instrument cut sheet with each character in the model number highlighted on the order section. This must be provided for each unique model number. Any special characters that are not published by the manufacturer but exist in the model number shall be accompanied bya clear description as provided by manufacturer. Documentation of this description shall be provided in the form of official communications with manufacturer such as email or printed literature. 6. Instrumentation such as diaphragm valves, multiport valves, and RTD/thermowells, where the orientation and dimensions are more clearly described usinga drawing, shall be provided with the appropriate drawings. This drawing shall document sizes and label port numbers, weir numbers, tag
976 | 409021 | I&C | 1.5 | SUBMITTALS | General | General Provide submittals of material or equipment in accordance with the main equipment specification. 1.5.1. Documentation Standard Symbols and Legends shall detail all symbology used in design documents and drawings includinga description of what each symbol represents. These shall conform to Owners plant standards if such standards exist.
979 | 409050 | BASIC I&C MATERIALS AND METHODS | 2.1 | GENERAL | Product Data | Control Room and Field Instruments: Provide all instruments as described in Section 409100, Instrument Index and Data Sheets, and in accordance with terms of the contract. In some cases, certain instruments shall be furnished only and installed by others. Coordinate these issues with the Owner or Owners representative. Calibration Instruments: The Contractor shall furnish all calibration equipment, test equipment, and all special tools peculiar to an instrument required to complete the work. Where required by the Owner, the Contractor shall provide all calibration certification information and documentation. Process Connections: Provide all materials required to complete the instrument process connections, sensing lines, and sensor installations in accordance with current instrument installation practices, manufacturers recommendations, and/or the installation details where provided. This shall include all required: Piping Tubing Fittings Isolation Manifolds Hardware and Supports Valves after the First Branch Valve All process wetted materials shall meet or exceed the corrosion, pressure, and temperature requirements of the process. The Contractor shall be aware that the construction and design of some instruments requires better corrosion, pressure, and temperature ratings than is required by the piping or vessel and shall assure that these requirements are satisfied.
984 | 424113 | TEMPERATURE CONTROL UNIT | 1.2 | SUBMITTALS | General | The following table outlines the required submittals for compliance with this specification. These submittals are defined in specification section 110010. This does not relieve the manufacturer from supplying any additional documentation as specified by the applicable codes and standards, or other submittal requirements as indicated in attached specifications. Providea review set of documents at FAT. Documents may change asa result of the FAT. Final revisions are to be shipped with the equipment and shall arrive no later than the equipment. * Denotes submittals that shall be submitted both electronically and as hard copy.
985 | 426013 | GMP PARTS WASHER | 1.2 | EQUIPMENT SCHEDULE | Schedules | The Manufacturer shall provide equipment as indicated in the associated Equipment Data Sheet.
986 | 426013 | GMP PARTS WASHER | 1.4 | SUBMITTALS | General | The associated Vendor Documentation Requirements (VDR) Specification outlines the required submittals for compliance with this specification. These submittals are defined in specification section 110010. This does not relieve the manufacturer from supplying any additional documentation as specified by the applicable codes and standards, or other submittal requirements as indicated in attached specifications. The manufacturer shall certify--in writing--design, fabrication and testing compliance with listed requirements. The manufacturer shall providea review set of documents at FAT. Documents may change asa result of the FAT. Final revisions are to be shipped with the equipment and shall arrive no later than the equipment.
987 | 426013 | GMP PARTS WASHER | 2.1 | BASIC SYSTEM DESCRIPTION | Product Data | Manufacturer shall submit based on the standard size that is equal to, or larger than, the listed nominal chamber dimensions. The GMP Washer shall be capable of producing chemically clean glassware, components or equipment without presoaking, scraping or other pretreatment. The washer shall be designed for internal water recirculation or once- through flow through appropriately designed rotary spray arms on top and bottom and load rack spindles, during all phases of the cycle. The equipment shall be supplied witha forced air-drying system. The washer furnished under this specification shall include washing chamber, control panel, filters, instrumentation, piping, wiring, insulation, water heater, drying air heater, air circulation blower(s), circulation water pump, air exhaust blower, supply and return connections to allow for internal hose washing and/or cleaning of product piping spool pieces, and all necessary appurtenances as required fora complete package. Vendor shall provide mobile carts, and loading racks as specified in the data sheets. The washer shall be capable of washing and drying items identified on the Equipment Data Sheet(s). The washer shall have flexible control to allow for programming of cycles that may include detergent wash, acid wash, rinses, once-through final rinse (e.g., WFI), exhaust and air drying of various cycle lengths. As indicated on the data sheet, the equipment shall be capable of connecting to multiple water quality supplies. The washer shall use filtered air propelled by blowers as the air source for the drying cycle, as indicated on the datasheet. Duct connection size, air flow rate and whether or not the air flow isa constant shall be included in the proposal. Test ports shall be provided for testing of the filters. Manufacturer shall provide all the component operating systems necessary to obtaina complete and operable unit, factory-tested and ready for connection to the building utility service lines. The system shall be identified with permanently mounted tags showing equipment numbers and description. Manufacturer shall provide suitable pipe and duct terminations for utilities toa single point of connection at each skid. Owner will provide appropriate roughing filters, let down regulators, and pressure relief valves. The utilities as designed are listed on the attached data sheet. Manufacturer shall verify equipment operation based on utility design specified in the data sheet.
988 | 432216 | LIQUID AGITATOR | 1.2 | EQUIPMENT SCHEDULE | Schedules | The Manufacturer shall provide equipment as indicated in the Equipment Schedule below. EQUIPMENT SCHEDULE EQUIPMENT P&ID CAPACITY NAME NUMBER NUMBER LA5V101AG01 34-0200-031 0-80 RPM Pooling Vessel 1 Agitator LA5V102AG01 34-0200-032 0-80 RPM Pooling Vessel 2 Agitator LA5V103AG01 34-0200-033 0-80 RPM Pooling Vessel 3 Agitator
989 | 434113 | STAINLESS STEEL PROCESS VESSEL | 1.2 | EQUIPMENT SCHEDULE | Schedules | The Manufacturer shall provide equipment as indicated in the Equipment Schedule below. EQUIPMENT SCHEDULE EQUIPMENT P&ID NUMBER CAPACITY NAME NUMBER LA5V101 34-0200-031 9,000 Liters Pooling Vessel 1 LA5V102 34-0200-032 9,000 Liters Pooling Vessel 2 LA5V103 34-0200-033 9,000 Liters Pooling Vessel 3
990 | 434113 | STAINLESS STEEL PROCESS VESSEL | 1.3 | SUBMITTALS | General | Refer to specification section 110010 and the Vendor Documentation Requirements (VDR) list for submittal requirements and definitions. This does not relieve the manufacturer from supplying any additional documentation as specified by the applicable codes and standards, or other submittal requirements as indicated in attached specifications. Providea review set of documents at FAT. Documents may change asa result of the FAT. Final revisions are to be shipped with the equipment and shall arrive no later than the equipment.
991 | 458050 | CIP SKID | 1.2 | SUBMITTALS | General | Reference specification section 110010 Equipment General Requirements for submittal requirements. This does not relieve the manufacturer from supplying any additional documentation as specified by the applicable codes and standards, or other submittal requirements as indicated in attached specifications. Providea review set of documents at FAT. Documents may change asa result of the FAT. Final revisions are to be shipped with the equipment and shall arrive no later than the equipment.
992 | 458050 | CIP SKID | 1.4 | EXTRA MATERIAL | Attic Stock | Manufacturer shall provide extra materials as listed below: Provide three extra rupture disks for each rupture disk assembly. Provide two (2) complete sets of gaskets and O-ring seals for the complete system, including O- rings for the heat exchanger. Provide end cap, sanitary clamp and gasket for all free sanitary connections, both on the vessel and on the piping. The Manufacturer shall providea minimum of two (2) filter cartridges for each filter indicated on the PIDs or data sheets; one (1) of use during FAT, and one to be installed in the field during start- up and commissioning activities.