## Sheet 1
S. No. | Spec # | Spec Name | Para | Sub Section Heading | Submittal Type | Submittal Description | Target Date | Subcontractor
44 | 024119 | SELECTIVE DEMOLITION | 1.10-A | WARRANTY | Warranty | Existing Warranties : Remove, replace, patch, and repair materials and surfaces cut or damaged during selective demolition, by methods and with materials and using approved contractors so as not to void existing warranties. Notify warrantor before proceeding. Existing warranties include the following: 1. TPO Roofing System
45 | 024119 | SELECTIVE DEMOLITION | 1.10-B | WARRANTY | Warranty | Notify warrantor on completion of selective demolition, and obtain documentation verifying that existing system has been inspected and warranty remains in effect. Submit documentation at Project closeout.
36 | 024119 | SELECTIVE DEMOLITION | 1.5-A | PREINSTALLATION MEETINGS | Meetings | Predemolition Conference : Conduct conference at Project site. 1. Inspect and discuss condition of construction to be selectively demolished. 2. Review structural load limitations of existing structure. 3. Review and finalize selective demolition schedule and verify availability of materials, demolition personnel, equipment, and facilities needed to make progress and avoid delays. 4. Review requirements of work performed by other trades that rely on substrates exposed by selective demolition operations. 5. Review areas where existing construction is to remain and requires protection.
37 | 024119 | SELECTIVE DEMOLITION | 1.6-A | INFORMATIONAL SUBMITTALS | Measurements | Proposed Protection Measures : Submit report, including Drawings, that indicates the measures proposed for protecting individuals and property, for environmental protection , for dust control and, for noise control. Indicate proposed locations and construction of barriers.
38 | 024119 | SELECTIVE DEMOLITION | 1.6-B | INFORMATIONAL SUBMITTALS | Schedules | Schedule of Selective Demolition Activities : Indicate the following: 1. Detailed sequence of selective demolition and removal work, with starting and ending dates for each activity. Ensure Owner's building manager's and on-site operations are uninterrupted. 2. Interruption of utility services. Indicate how long utility services will be interrupted. 3. Coordination for shutoff, capping, and continuation of utility services. 4. Use of elevator and stairs. 5. Coordination of Owner's continuing occupancy of portions of existing building and of Owner's partial occupancy of completed Work.
39 | 024119 | SELECTIVE DEMOLITION | 1.6-C | INFORMATIONAL SUBMITTALS | Photos | Predemolition Photographs or Video : Show existing conditions of adjoining construction, including finish surfaces, that might be misconstrued as damage caused by demolition operations. Submit before Work begins.
40 | 024119 | SELECTIVE DEMOLITION | 1.6-D | INFORMATIONAL SUBMITTALS | Statement Of Refrigerant Recovery | Statement of Refrigerant Recovery : Signed by refrigerant recovery technician responsible for recovering refrigerant, stating that all refrigerant that was present was recovered and that recovery was performed according to EPA regulations. Include name and address of technician and date refrigerant was recovered.
41 | 024119 | SELECTIVE DEMOLITION | 1.6-E | INFORMATIONAL SUBMITTALS | Warranty | Warranties : Documentation indicating that existing warranties are still in effect after completion of selective demolition.
42 | 024119 | SELECTIVE DEMOLITION | 1.7-A | CLOSEOUT SUBMITTALS | Inventory | Inventory : Submita list of items that have been removed and salvaged.
46 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-A.1 | SUBMITTALS | Product Data | 1. Submit product data indicating product standards, physical and chemical characteris-- tics, technical specifications, limitations, installation instructions, maintenance in- structions and general recommendations regarding each individual material.
47 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-A.2 | SUBMITTALS | General | 2. Only epoxy resins will be accepted for construction of FRP systems referenced in this- specification. Other resins, such as polyesters/vinyl esters, are not allowed as substi- tutes. The manufacturer shall clearly define the epoxy resin working time. Any batch that exceeds the batch life shall not be used.
49 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-A.4 | SUBMITTALS | General | 4. Written consent from the FRP manufacturer that the surface bonded FRP composite- systems are installed by trained certified applicators as per Section 2.2
52 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-A.7 | SUBMITTALS | Performance Data | 7. Large-scale test results validating the fiber anchor performance on relevant test spec-- imens. Compatibility between composite anchors and the composite system must be verified through large-scale testing for similar applications.
53 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-A.8 | SUBMITTALS | General | 8. At the termination of the project, the contractor shall providea field quality control- report showing compliance with all aspects of the manufacturers certification re- quirements. This report shall be stamped bya civil engineer registered in the state where the work is performed.
54 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-B | SUBMITTALS | Drawings | Design and Working Drawings : - 1. Design and working drawings shall be based on performance as per Section 1.6. 2. Stamped and signed structural calculations and drawings bya professional Civil En- gineer. Design shall be based on the clearly written performance criteria defined on the structural drawings. 3. Working shop drawings and calculations prepared and sealed bya professional engi- neer detailing the type, locations, dimensions, numbers of layers, and orientation of all FRP materials and coatings to be installed. The shop drawings must also indicatea total weight per unit length of each size of anchor (if required) to be used in the pro- ject.
55 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-C.1 | SUBMITTALS | General | 1. Manufacturer shall havea minimum of ten (10) years experience confirmed by pro-- ject references.
56 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-C.2 | SUBMITTALS | Reports | 2. Providea current ICC Evaluation Service Report, as per Section 1.5.3-
57 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-C.3 | SUBMITTALS | General | 3. If fire protection is required, provide approved UL rated assembly data for any re-- quired fire-resistant finish (1, 2, 3 or 4 hour rated assembly per ASTM E119 or Class A Building, Flame Spread & Smoke Development per ASTM E84) as proposed with the FRP system.
58 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-C.4 | SUBMITTALS | General | 4. Properties of the composite materials as determined by independent laboratory test-- ing in accordance with ASTM D7565 and/or ASTM D3039 (tensile modulus, stress and strain) for the proposed fiber composite system. A minimum of 20 tests for each must be submitted.
59 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-C.5 | SUBMITTALS | Maintenance Data | 5. Installation procedures, maintenance instructions, and general recommendations re-- garding each material to be used.
60 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-C.6 | SUBMITTALS | General | 6. Manufacturers Material Safety Data Sheets (MSDS) for all materials to be used.-
61 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-C.7 | SUBMITTALS | Product Data | 7. Manufacturers product data sheet indicating physical, mechanical and chemical- characteristics of all materials used in the FRP system.
62 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.5-C.8 | SUBMITTALS | Certifications | 8. Certification by the manufacturer that supplied products complies with local regula-- tions controlling use of volatile organic compounds (VOCs).
63 | 030100 | ADVANCED COMPOSITE MATERIALS | 1.6-A | PERFORMANCE | Delegated-Design Submittal | Design the composite system to achieve the structural performance shown on the structural drawings. Design calculations for the composite system shall be submitted for approval by the engineer of record and shall be stamped bya registered Civil or Structural Engineer. The composite anchors must meet the minimum total weight per unit length for each size of anchor as per submitted design.
70 | 032000 | CONCRETE REINFORCING | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For the following: 1. Each type of steel reinforcement. 2. Bar supports.
71 | 032000 | CONCRETE REINFORCING | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Comply with ACI SP-066: 1. Include placing drawings that detail fabrication, bending, and placement. 2. Include bar sizes, lengths, materials, grades, bar schedules, stirrup spacing, bent bar diagrams, bar arrangement, location of splices, lengths of lap splices, details of mechanical splice couplers, details of welding splices, tie spacing, hoop spacing, and supports for concrete reinforcement. 3. For structural thermal break insulated connection system, indicate general configuration, insulation dimensions, tension bars, compression pads, shear bars, and dimensions.
72 | 032000 | CONCRETE REINFORCING | 1.3-C | ACTION SUBMITTALS | Construction Joint Layout | Construction Joint Layout : Indicate proposed construction joints required to build the structure. 1. Location of construction joints is subject to approval of the Architect.
73 | 032000 | CONCRETE REINFORCING | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Statements : For testing and inspection agency.
74 | 032000 | CONCRETE REINFORCING | 1.4-B | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each of the following, signed by manufacturers: 1. Epoxy-Coated Reinforcement: CRSI's "Epoxy Coating Plant Certification." 2. Dual-Coated Reinforcement: CRSI's "Epoxy Coating Plant Certification."
77 | 033000 | CAST-IN-PLACE CONCRETE | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Require representatives of each entity directly concerned with cast-in-place concrete to attend, including the following: a. Contractor's superintendent. b. Concrete Subcontractor. 2. Review the following: a. Special inspection and testing and inspecting agency procedures for field quality control. b. Construction joints, control joints, isolation joints, and joint-filler strips. c. Semirigid joint fillers. d. Vapor-retarder installation. e. Anchor rod and anchorage device installation tolerances. f. Cold and hot weather concreting procedures. g. Concrete finishes and finishing. h. Curing procedures. i. Forms and form-removal limitations. j. Shoring and reshoring procedures. k. Methods for achieving specified floor and slab flatness and levelness. l. Floor and slab flatness and levelness measurements. m. Concrete repair procedures. n. Concrete protection. o. Initial curing and field curing of field test cylinders (ASTM C31/C31M.) p. Protection of field cured field test cylinders.
78 | 033000 | CAST-IN-PLACE CONCRETE | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each of the following. 1. Portland cement. 2. Fly ash. 3. Slag cement. 4. Blended hydraulic cement. 5. Silica fume. 6. Performance-based hydraulic cement 7. Aggregates. 8. Admixtures: a. Include limitations of use, including restrictions on cementitious materials, supplementary cementitious materials, air entrainment, aggregates, temperature at time of concrete placement, relative humidity at time of concrete placement, curing conditions, and use of other admixtures. 9. Vapor retarders. 10. Curing materials. 11. Joint fillers. 12. Repair materials.
79 | 033000 | CAST-IN-PLACE CONCRETE | 1.5-B | ACTION SUBMITTALS | Mix Design | Design Mixtures : For each concrete mixture, include the following: 1. Mixture identification. 2. Minimum 28-day compressive strength. 3. Durability exposure class. 4. Maximum w/cm. 5. Calculated equilibrium unit weight, for lightweight concrete. 6. Slump limit. 7. Air content. 8. Nominal maximum aggregate size. 9. Intended placement method. 10. Submit alternate design mixtures when characteristics of materials, Project conditions, weather, test results, or other circumstances warrant adjustments.
80 | 033000 | CAST-IN-PLACE CONCRETE | 1.5-C | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Construction Joint Layout: Indicate proposed construction joints required to construct the structure. a. Location of construction joints is subject to approval of the Architect.
81 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For the following: 1. Installer: Include copies of applicable ACI certificates. 2. Ready-mixed concrete manufacturer. 3. Testing agency: Include copies of applicable ACI certificates.
82 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each of the following, signed by manufacturers: 1. Cementitious materials. 2. Admixtures. 3. Curing compounds. 4. Bonding agents. 5. Adhesives. 6. Vapor retarders. 7. Semirigid joint filler. 8. Joint-filler strips. 9. Repair materials.
83 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-C | INFORMATIONAL SUBMITTALS | Test Reports | Material Test Reports : For the following, froma qualified testing agency: 1. Portland cement. 2. Fly ash. 3. Slag cement. 4. Blended hydraulic cement. 5. Silica fume. 6. Performance-based hydraulic cement. 7. Aggregates. 8. Admixtures: a. Permeability-Reducing Admixture: Include independent test reports, indicating compliance with specified requirements, including dosage rate used in test.
84 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-D | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
85 | 033000 | CAST-IN-PLACE CONCRETE | 1.6-E | INFORMATIONAL SUBMITTALS | Meeting Minutes | Minutes of preinstallation conference.
96 | 33543 | POLISHED CONCRETE FINISHING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
97 | 033543 | POLISHED CONCRETE FINISHING | 1.4-B | ACTION SUBMITTALS | Schedules | Polishing Schedule : Submit plan showing polished concrete surfaces and schedule of polishing operations for each area of polished concrete before start of polishing operations. Include locations of all joints, including construction joints.
98 | 033543 | POLISHED CONCRETE FINISHING | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of product requiring color selection.
99 | 033543 | POLISHED CONCRETE FINISHING | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
100 | 033543 | POLISHED CONCRETE FINISHING | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each of the following, signed by manufacturers: 1. Repair materials. 2. Stain materials. 3. Liquid floor treatments.
101 | 033543 | POLISHED CONCRETE FINISHING | 1.6-A | QUALITY ASSURANCE | Mockups | Mockups : Before casting concrete, build mockups to verify selections made under Sample submittals and to demonstrate typical joints, surface finish, tolerances, and standard of workmanship. Build mockups to comply with the following requirements, using materials indicated for the completed Work: 1. Build mockups in the location and of the size indicated or, if not indicated, as directed by Architect. 2. Demonstrate curing, finishing, and protecting of polished concrete. 3. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
102 | 042200 | CONCRETE UNIT MASONRY | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
103 | 042200 | CONCRETE UNIT MASONRY | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
104 | 042200 | CONCRETE UNIT MASONRY | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For the following: 1. Masonry Units: Show sizes, profiles, coursing, and locations of special shapes. 2. Reinforcing Steel: Detail bending, lap lengths, and placement of unit masonry reinforcing bars. Comply with ACI 315. Show elevations of reinforced walls. 3. Fabricated Flashing: Detail corner units, end-dam units, and other special applications.
105 | 042200 | CONCRETE UNIT MASONRY | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For testing agency.
106 | 042200 | CONCRETE UNIT MASONRY | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each type and size of the following: 1. Masonry units. a. Include data on material properties. b. For masonry units, include data and calculations establishing average net-area compressive strength of units. 2. Integral water repellant used in CMUs. 3. Preblended, dry mortar mixes. Include description of type and proportions of ingredients. 4. Grout mixes. Include description of type and proportions of ingredients. 5. Reinforcing bars. 6. Joint reinforcement. 7. Anchors, ties, and metal accessories.
107 | 042200 | CONCRETE UNIT MASONRY | 1.6-C | INFORMATIONAL SUBMITTALS | Mix Design | Mix Designs : For each type of mortar and grout. Include description of type and proportions of ingredients. 1. Include test reports for mortar mixes required to comply with property specification. Test according to ASTM C109/C109M for compressive strength, ASTM C1506 for water retention, and ASTM C91/C91M for air content. 2. Include test reports, according to ASTM C1019, for grout mixes required to comply with compressive strength requirement.
108 | 042200 | CONCRETE UNIT MASONRY | 1.6-D | INFORMATIONAL SUBMITTALS | General | Statement of Compressive Strength of Masonry : For each combination of masonry unit type and mortar type, provide statement of average net-area compressive strength of masonry units, mortar type, and resulting net-area compressive strength of masonry determined according to TMS 602/ACI 530.1/ASCE 6.
109 | 042200 | CONCRETE UNIT MASONRY | 1.6-E | INFORMATIONAL SUBMITTALS | Cold-Weather And Hot-Weather Procedures | Cold-Weather and Hot-Weather Procedures : Detailed description of methods, materials, and equipment to be used to comply with requirements.
120 | 051200 | STRUCTURAL STEEL FRAMING | 1.5-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
121 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-A | ACTION SUBMITTALS | Product Data | Product Data : - 1. Structural-steel materials. 2. High-strength, bolt-nut-washer assemblies. 3. Shear stud connectors. 4. Anchor rods. 5. Threaded rods. 6. Forged-steel hardware. 7. Shop primer. 8. Galvanized-steel primer. 9. Galvanized repair paint. 10. Shrinkage-resistant grout.
122 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Show fabrication of structural-steel components. 1. Include details of cuts, connections, splices, camber, holes, and other pertinent data. 2. Include embedment Drawings. 3. Indicate welds by standard AWS symbols, distinguishing between shop and field welds, and show size, length, and type of each weld. Show backing bars that are to be removed and supplemental fillet welds where backing bars are to remain. 4. Indicate type, size, and length of bolts, distinguishing between shop and field bolts. Identify pretensioned and slip-critical, high-strength bolted connections. 5. Identify members not to be shop primed.
123 | 051200 | STRUCTURAL STEEL FRAMING | 1.6-C | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For structural-steel connections indicated on Drawings to comply with design loads, include analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
124 | 051200 | STRUCTURAL STEEL FRAMING | 1.7-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer fabricator shop-painting applicators professional engineer testing agency.
125 | 051200 | STRUCTURAL STEEL FRAMING | 1.7-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
126 | 051200 | STRUCTURAL STEEL FRAMING | 1.7-C | INFORMATIONAL SUBMITTALS | Certificates | Paint Compatibility Certificates : From manufacturers of topcoats applied over shop primers, certifying that shop primers are compatible with topcoats.
127 | 051200 | STRUCTURAL STEEL FRAMING | 1.7-D | INFORMATIONAL SUBMITTALS | Test Reports | Mill test reports for structural-steel materials, including chemical and physical properties.
128 | 051200 | STRUCTURAL STEEL FRAMING | 1.7-E | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For the following: 1. Bolts, nuts, and washers, including mechanical properties and chemical analysis. 2. Direct-tension indicators. 3. Shear stud connectors. 4. .
129 | 051200 | STRUCTURAL STEEL FRAMING | 1.7-F | INFORMATIONAL SUBMITTALS | General | Survey of existing conditions.
130 | 051200 | STRUCTURAL STEEL FRAMING | 1.7-G | INFORMATIONAL SUBMITTALS | Reports | Source quality-control reports.
131 | 051200 | STRUCTURAL STEEL FRAMING | 1.7-H | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
139 | 053100 | STEEL DECKING | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For the following: 1. Roof deck. 2. Composite floor deck.
140 | 053100 | STEEL DECKING | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include layout and types of deck panels, anchorage details, reinforcing channels, pans, cut deck openings, special jointing, accessories, and attachments to other construction.
141 | 053100 | STEEL DECKING | 1.4-A | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
142 | 053100 | STEEL DECKING | 1.4-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of steel deck.
143 | 053100 | STEEL DECKING | 1.4-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For tests performed bya qualified testing agency, indicating that each of the following complies with requirements: 1. Power-actuated mechanical fasteners.
144 | 053100 | STEEL DECKING | 1.4-D | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
150 | 054000 | COLD-FORMED METAL FRAMING TO NONSTRUCTURAL FRAMI | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
151 | 054000 | COLD-FORMED METAL FRAMING TO NONSTRUCTURAL FRAMI | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For the following: 1. Cold-formed steel framing materials. 2. Interior non-load-bearing wall framing. 3. Vertical deflection clips. 4. Single deflection track. 5. Drift clips. 6. Soffit framing. 7. Power-actuated anchors.
152 | 054000 | COLD-FORMED METAL FRAMING TO NONSTRUCTURAL FRAMI | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include layout, spacings, sizes, thicknesses, and types of cold-formed steel framing; fabrication; and fastening and anchorage details, including mechanical fasteners. 2. Indicate reinforcing channels, opening framing, supplemental framing, strapping, bracing, bridging, splices, accessories, connection details, and attachment to adjoining work.
153 | 054000 | COLD-FORMED METAL FRAMING TO NONSTRUCTURAL FRAMI | 1.4-C | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For cold-formed steel framing.
154 | 054000 | COLD-FORMED METAL FRAMING TO NONSTRUCTURAL FRAMI | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For testing agency.
155 | 054000 | COLD-FORMED METAL FRAMING TO NONSTRUCTURAL FRAMI | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
156 | 054000 | COLD-FORMED METAL FRAMING TO NONSTRUCTURAL FRAMI | 1.5-C | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of code-compliance certification for studs and tracks.
157 | 054000 | COLD-FORMED METAL FRAMING TO NONSTRUCTURAL FRAMI | 1.5-D | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each listed product, for tests performed bya qualified testing agency. Expansion anchors. 1. Power-actuated anchors. 2. Mechanical fasteners. 3. Vertical deflection clips. 4. Horizontal drift deflection clips 5. Miscellaneous structural clips and accessories.
158 | 054000 | COLD-FORMED METAL FRAMING TO NONSTRUCTURAL FRAMI | 1.5-E | INFORMATIONAL SUBMITTALS | Reports | Research Reports : - 1. For nonstandard cold-formed steel framing power-actuated fasteners, from ICC-ES or other qualified testing agency acceptable to authorities having jurisdiction. 2. For sill sealer gasket/termite barrier, showing compliance with ICC-ES AC380.
168 | 055000 | METAL FABRICATIONS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For the following: 1. Nonslip aggregates and nonslip-aggregate surface finishes. 2. Fasteners. 3. Shop primers. 4. Shrinkage-resisting grout. 5. Prefabricated building columns. 6. Slotted channel framing. 7. Alternating tread devices. 8. Metal bollards. 9. Abrasive metal nosings.
169 | 055000 | METAL FABRICATIONS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Show fabrication and installation details. Include plans, elevations, sections, and details of metal fabrications and their connections. Show anchorage and accessory items. Provide Shop Drawings for the following: 1. Steel framing and supports for ceiling-hung toilet compartments. 2. Steel framing and supports for operable partitions. 3. Steel framing and supports for overhead doors. 4. Steel framing and supports for countertops. 5. Steel framing and supports for laboratory equipment. 6. Elevator machine beams, hoist beams and divider beams. 7. Steel shapes for supporting elevator door sills. 8. Prefabricated building columns. 9. Shelf angles. 10. Alternating tread devices. 11. Metal floor plate and supports. 12. Elevator pit sump covers. 13. Miscellaneous steel trim including steel angle corner guards and loading-dock edge angles. 14. Metal bollards. 15. Abrasive metal nosings.
170 | 055000 | METAL FABRICATIONS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type and finish of extruded nosing.
171 | 055000 | METAL FABRICATIONS | 1.4-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For alternating tread devices, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
172 | 055000 | METAL FABRICATIONS | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For professional engineer's experience with providing delegated-design engineering services of the kind indicated, including documentation that engineer is licensed in the jurisdiction in which Project is located.
173 | 055000 | METAL FABRICATIONS | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Mill Certificates : Signed by stainless steel manufacturers, certifying that products furnished comply with requirements.
174 | 055000 | METAL FABRICATIONS | 1.5-C | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
175 | 055000 | METAL FABRICATIONS | 1.5-D | INFORMATIONAL SUBMITTALS | Certificates | Paint Compatibility Certificates : From manufacturers of topcoats applied over shop primers, certifying that shop primers are compatible with topcoats.
176 | 055000 | METAL FABRICATIONS | 1.5-E | INFORMATIONAL SUBMITTALS | Reports | Research Reports : For post-installed anchors.
178 | 055113 | METAL PAN STAIRS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For metal pan stairs and the following: 1. Woven-wire mesh. 2. Prefilled metal-pan-stair treads. 3. Abrasive nosings. 4. Shop primer products. 5. Precast terrazzo treads. 6. Handrail wall brackets. 7. Grout.
179 | 055113 | METAL PAN STAIRS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, details, and attachments to other work. 2. Indicate sizes of metal sections, thickness of metals, profiles, holes, and field joints. 3. Include plan at each level. 4. Indicate locations of anchors, weld plates, and blocking for attachment of wall-mounted handrails. 5. Indicate profile and dimensions of precast terrazzo treads.
180 | 055113 | METAL PAN STAIRS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type and finish of nosing and precast terrazzo tread.
181 | 055113 | METAL PAN STAIRS | 1.4-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For stairs, railings and guards, precast terrazzo treads including analysis data signed and sealed by the qualified professional engineer responsible for their preparation. Verify stair stringer sizes shown on structural drawings. Delegated designer can reduce steel sizes and bracing as engineer of record.
182 | 055113 | METAL PAN STAIRS | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For professional engineer's experience with providing delegated-design engineering services of the kind indicated, including documentation that engineer is licensed in the State in which Project is located.
183 | 055113 | METAL PAN STAIRS | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
184 | 055113 | METAL PAN STAIRS | 1.5-C | INFORMATIONAL SUBMITTALS | Certificates | Paint Compatibility Certificates : From manufacturers of topcoats applied over shop primers, certifying that shop primers are compatible with topcoats.
187 | 055119 | METAL GRATING STAIRS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For metal grating stairs and the following: 1. Gratings. 2. Shop primer products. 3. Grout.
188 | 055119 | METAL GRATING STAIRS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, details, and attachment to other work. 2. Indicate sizes of metal sections, thickness of metals, profiles, holes, and field joints. 3. Include plan at each level. 4. Indicate locations of anchors, weld plates, and blocking for attachment of wall-mounted handrails.
189 | 055119 | METAL GRATING STAIRS | 1.4-C | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For stairs, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
190 | 055119 | METAL GRATING STAIRS | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For professional engineer's experience with providing delegated-design engineering services of the kind indicated, including documentation that engineer is licensed in the State in which Project is located.
191 | 055119 | METAL GRATING STAIRS | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
192 | 055119 | METAL GRATING STAIRS | 1.5-C | INFORMATIONAL SUBMITTALS | Certificates | Paint Compatibility Certificates : From manufacturers of topcoats applied over shop primers, certifying that shop primers are compatible with topcoats.
195 | 055213 | PIPE AND TUBE RAILINGS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : - 1. Manufacturer's product lines of mechanically connected railings. 2. Fasteners. 3. Post-installed anchors. 4. Handrail brackets. 5. Shop primer. 6. Intermediate coats and topcoats. 7. Nonshrink, nonmetallic grout. 8. Anchoring cement. 9. Metal finishes. 10. Paint products.
196 | 055213 | PIPE AND TUBE RAILINGS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include plans, elevations, sections, details, and attachments to other work.
197 | 055213 | PIPE AND TUBE RAILINGS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed finish required. 1. Assembled Sample of railing system, made from full-size components, including top rail, post, handrail, and infill. Sample need not be full height. a. Show method of connecting members at intersections.
198 | 055213 | PIPE AND TUBE RAILINGS | 1.4-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For railings, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation including base connection design.
199 | 055213 | PIPE AND TUBE RAILINGS | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For delegated-design professional engineer.
200 | 055213 | PIPE AND TUBE RAILINGS | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
201 | 055213 | PIPE AND TUBE RAILINGS | 1.5-C | INFORMATIONAL SUBMITTALS | Certificates | Mill Certificates : Signed by manufacturers of stainless steel products, certifying that products furnished comply with requirements.
202 | 055213 | PIPE AND TUBE RAILINGS | 1.5-D | INFORMATIONAL SUBMITTALS | Certificates | Paint Compatibility Certificates : From manufacturers of topcoats applied over shop primers, certifying that shop primers are compatible with topcoats.
203 | 055213 | PIPE AND TUBE RAILINGS | 1.5-E | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For tests on railings performed bya qualified testing agency, in accordance with ASTM E894 and ASTM E935.
204 | 055213 | PIPE AND TUBE RAILINGS | 1.5-F | INFORMATIONAL SUBMITTALS | Reports | Research Reports : For post-installed anchors, from ICC-ES or other qualified testing agency acceptable to authorities having jurisdiction.
206 | 055313 | BAR GRATINGS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For the following: 1. Clips and anchorage devices for gratings. 2. Paint products.
207 | 055313 | BAR GRATINGS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include plans, sections, details, and attachments to other work.
208 | 055313 | BAR GRATINGS | 1.5-A | INFORMATIONAL SUBMITTALS | Certificates | Mill Certificates : Signed by manufacturers of stainless steel certifying that products furnished comply with requirements.
209 | 055313 | BAR GRATINGS | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
211 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : - 1. Glass products. 2. Glazing cement and accessories for structural glass railings. 3. Sealant and accessories for structural glass railings. 4. Fasteners. 5. Nonshrink, nonmetallic grout. 6. Anchoring cement.
212 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include plans, elevations, sections, and attachment details.
213 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed finish required. 1. Assembled Samples of railing systems, made from full-size components, including top rail, post, handrail, glass-infill panels. Show method of finishing members at intersections. Samples need not be full height.
214 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.5-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For installed products indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
215 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For professional engineer.
216 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Mill Certificates : Signed by manufacturers of stainless steel products, certifying that products furnished comply with requirements.
217 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.6-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For tests performed bya qualified testing agency, in accordance with ASTM E894, ASTM E935, ASTM E2353, and ASTM E2358.
218 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.6-D | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : From ICC-ES or other qualified testing agency acceptable to authorities having jurisdiction. 1. For glazed decorative metal railings.
219 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.6-E | INFORMATIONAL SUBMITTALS | Test Reports | Preconstruction test reports.
220 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.7-A | QUALITY ASSURANCE | Mockups | Mockups : Build mockups to verify selections made under Sample submittals, to demonstrate aesthetic effects, and to set quality standards for fabrication and installation. 1. Build mockups for each form and finish of structural glass railing consisting of top rail, structural glass, base channel, and anchorage system components that are full height and are not less than 24 inches in length. 2. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
221 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 1.9-A | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty for Laminated Glass : Glazed decorative metal railing manufacturer agrees to replace laminated-glass units that deteriorate within specified warranty period. Deterioration of laminated glass is defined as defects developed from normal use that are not attributed to glass breakage or to maintaining and cleaning laminated glass contrary to manufacturer's written instructions. Defects include edge separation, delamination materially obstructing vision through glass, and blemishes exceeding those allowed by referenced laminated glass standard. 1. Warranty Period: 10 years from date of Substantial Completion.
222 | 057313 | GLAZED DECORATIVE METAL RAILINGS | 2.2-A | PERFORMANCE REQUIREMENTS | Delegated-Design Submittal | Delegated Design : Engagea qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design glazed decorative metal railings, including attachment to building construction.
227 | 061053 | MISCELLANEOUS ROUGH CARPENTRY | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of process and factory-fabricated product. Indicate component materials and dimensions and include construction and application details. 1. Include data for wood-preservative treatment from chemical treatment manufacturer and certification by treating plant that treated materials comply with requirements. Indicate type of preservative used and net amount of preservative retained. 2. Include data for fire-retardant treatment from chemical treatment manufacturer and certification by treating plant that treated materials comply with requirements. Include physical properties of treated materials based on testing bya qualified independent testing agency. 3. For fire-retardant treatments, include physical properties of treated lumber both before and after exposure to elevated temperatures, based on testing bya qualified independent testing agency according to ASTM D5664. 4. For products receivinga waterborne treatment, include statement that moisture content of treated materials was reduced to levels specified before shipment to Project site.
228 | 061053 | MISCELLANEOUS ROUGH CARPENTRY | 1.5-A | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For the following, from ICC-ES: 1. Preservative-treated wood. 2. Fire-retardant-treated wood. 3. Power-driven fasteners. 4. Post-installed anchors. 5. Metal framing anchors.
230 | 062023 | INTERIOR FINISH CARPENTRY | 1.3-A | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color and texture specified.
231 | 062023 | INTERIOR FINISH CARPENTRY | 1.3-B | ACTION SUBMITTALS | Samples | Samples for Verification : - 1. For each species and cut of lumber and panel products with nonfactory-applied finish, with half of exposed surface finished; 50 sq. in. for lumber and 8 by 10 inches for panels.
232 | 064113 | WOOD-VENEER-FACED ARCHITECTURAL CABINETS | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include data for fire-retardant treatment from chemical-treatment manufacturer and certification by treating plant that treated materials comply with requirements.
233 | 064113 | WOOD-VENEER-FACED ARCHITECTURAL CABINETS | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For architectural cabinets. 1. Include plans, elevations, sections, and attachment details. 2. Show details. 3. Show locations and sizes of furring, blocking, and hanging strips, including concealed blocking and reinforcement specified in other Sections. 4. Show locations and sizes of cutouts and holes for items installed in architectural cabinets. 5. Show veneer leaves with dimensions, grain direction, exposed face, and identification numbers indicating the flitch and sequence within the flitch for each leaf. 6. Apply AWI Quality Certification Program label to Shop Drawings.
234 | 064113 | WOOD-VENEER-FACED ARCHITECTURAL CABINETS | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of exposed finish.
235 | 064113 | WOOD-VENEER-FACED ARCHITECTURAL CABINETS | 1.5-D | ACTION SUBMITTALS | Samples | Samples for Verification : For the following: 1. Veneer Leaves: Representative of and selected from flitches to be used for transparent- finished cabinets. 2. Lumber and Panel Products with Shop-Applied Opaque Finish: 5 inches wide by 12 inches long for lumber and 8 by 10 inches for panels, for each finish system and color. a. Finish entire exposed surface. 3. Corner Pieces: a. Cabinet-front frame joints between stiles and rails and at exposed end pieces, 18 inches high by 18 inches wide by 6 inches deep. b. Miter joints for standing trim. 4. Exposed Cabinet Hardware and Accessories: One full-size unit for each type and finish.
236 | 064113 | WOOD-VENEER-FACED ARCHITECTURAL CABINETS | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For manufacturer and installer.
237 | 064113 | WOOD-VENEER-FACED ARCHITECTURAL CABINETS | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of product.
238 | 064113 | WOOD-VENEER-FACED ARCHITECTURAL CABINETS | 1.6-C | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For fire-retardant-treated materials, from ICC-ES.
239 | 064113 | WOOD-VENEER-FACED ARCHITECTURAL CABINETS | 1.6-D | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
240 | 064113 | WOOD-VENEER-FACED ARCHITECTURAL CABINETS | 1.7-A | CLOSEOUT SUBMITTALS | Certificates | Quality Standard Compliance Certificates : AWI Quality Certification Program certificates.
244 | 064116 | PLASTIC-LAMINATE-CLAD ARCHITECTURAL CABINETS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include data for fire-retardant treatment from chemical-treatment manufacturer and certification by treating plant that treated materials comply with requirements.
245 | 064116 | PLASTIC-LAMINATE-CLAD ARCHITECTURAL CABINETS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, and attachment details. 2. Show large-scale details. 3. Show locations and sizes of furring, blocking, and hanging strips, including concealed blocking and reinforcement specified in other Sections. 4. Show locations and sizes of cutouts and holes for items installed in plastic-laminate architectural cabinets. 5. Apply AWI Quality Certification Program label to Shop Drawings.
246 | 064116 | PLASTIC-LAMINATE-CLAD ARCHITECTURAL CABINETS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For the following: 1. Plastic Laminates: 8 by 10 inches, for each type, color, pattern, and surface finish required. a. Provide one sample applied to core material with specified edge material applied to one edge. 2. Corner Pieces: a. Cabinet-front frame joints between stiles and rails and at exposed end pieces, 18 inches high by 18 inches wide by 6 inches deep. b. Miter joints for standing trim. 3. Exposed Cabinet Hardware and Accessories: One full-size unit for each type and finish.
247 | 064116 | PLASTIC-LAMINATE-CLAD ARCHITECTURAL CABINETS | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For manufacturer and Installer.
248 | 064116 | PLASTIC-LAMINATE-CLAD ARCHITECTURAL CABINETS | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For the following: 1. Composite wood products. 2. Adhesives.
249 | 064116 | PLASTIC-LAMINATE-CLAD ARCHITECTURAL CABINETS | 1.5-C | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For fire-retardant-treated materials, from ICC-ES.
250 | 064116 | PLASTIC-LAMINATE-CLAD ARCHITECTURAL CABINETS | 1.5-D | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
251 | 064116 | PLASTIC-LAMINATE-CLAD ARCHITECTURAL CABINETS | 1.6-A | CLOSEOUT SUBMITTALS | Certificates | Quality Standard Compliance Certificates : AWI Quality Certification Program certificates.
265 | 070150.19 | PREPARATION FOR REROOFING | 1.11-A | WARRANTY | Warranty | Existing Warranties : Remove, replace, patch, and repair materials and surfaces cut or damaged during reroofing, by methods and with materials so as not to void existing roofing system warranty issued by existing warranted roof system. 1. Notify warrantor before proceeding with the Work. 2. Notify warrantor of existing roofing system on completion of reroofing, and obtain documentation verifying that existing roofing system has been inspected and warranty remains in effect. a. Submit documentation at Project closeout.
255 | 070150.19 | PREPARATION FOR REROOFING | 1.5-A | PREINSTALLATION MEETINGS | Meetings | Preliminary Roofing Conference : Before starting removal Work, conduct conference at Project site. 1. Meet with Owner, Architect, Construction Manager, Owner's insurer if applicable, testing and inspecting agency representative, roofing Installer, and installers whose work interfaces with or affects roofing, including installers of roof accessories and roof- mounted equipment. 2. Review methods and procedures related to roofing tear-off, including, but not limited to, the following: a. Reroofing preparation, including roofing system manufacturer's written instructions. b. Temporary protection requirements for existing roofing system components that are to remain. c. Existing roof drains and roof drainage during each stage of reroofing, and roof- drain plugging and plug removal. d. Construction schedule and availability of materials, Installer's personnel, equipment, and facilities needed to avoid delays. e. Existing roof deck conditions requiring Architect notification. f. Existing roof deck removal procedures and Owner notifications. g. Condition and acceptance of existing roof deck and base flashing substrate for reuse. h. Structural loading limitations of roof deck during reroofing. i. Base flashings, special roofing details, drainage, penetrations, equipment curbs, and condition of other construction that affect reroofing. j. HVAC shutdown and sealing of air intakes. k. Shutdown of fire-suppression, -protection, and -alarm and -detection systems. l. Asbestos removal and discovery of asbestos-containing materials. m. Governing regulations and requirements for insurance and certificates if applicable. n. Existing conditions that may require Architect notification before proceeding.
256 | 070150.19 | PREPARATION FOR REROOFING | 1.6-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
257 | 070150.19 | PREPARATION FOR REROOFING | 1.6-B | ACTION SUBMITTALS | Temporary Roofing Submittal | Temporary Roofing Submittal : Product data and description of temporary roofing system. 1. If temporary roof remains in place, include surface preparation requirements needed to receive permanent roof, and submita letter from roofing manufacturer stating acceptance of the temporary roof and that its inclusion does not adversely affect the new roofing system's resistance to fire and wind or its FM Approvals rating.
258 | 070150.19 | PREPARATION FOR REROOFING | 1.7-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer. 1. Include certificate that Installer is approved by warrantor of existing roofing system. 2. Include certificate that Installer is licensed to perform asbestos abatement.
259 | 070150.19 | PREPARATION FOR REROOFING | 1.7-B | INFORMATIONAL SUBMITTALS | Test Reports | Field Test Reports : - 1. Fastener pull-out test report.
260 | 070150.19 | PREPARATION FOR REROOFING | 1.7-C | INFORMATIONAL SUBMITTALS | Photos | Photographs or Videotape : Show existing conditions of adjoining construction and site improvements, including exterior and interior finish surfaces, that might be misconstrued as having been damaged by reroofing operations. 1. Submit before Work begins.
261 | 070150.19 | PREPARATION FOR REROOFING | 1.7-D | INFORMATIONAL SUBMITTALS | Landfill Records | Landfill Records : Indicate receipt and acceptance of demolished roofing materials and hazardous wastes, such as asbestos-containing materials, bya landfill facility licensed to accept them.
262 | 070150.19 | PREPARATION FOR REROOFING | 1.8-A | CLOSEOUT SUBMITTALS | Warranty | Certified statement from existing warranted roof system stating that existing roof warranty has not been affected by Work performed under this Section.
266 | 071616 | CRYSTALLINE WATERPROOFING | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
267 | 071616 | CRYSTALLINE WATERPROOFING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, and installation instructions.
268 | 071616 | CRYSTALLINE WATERPROOFING | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Applicator.
269 | 071616 | CRYSTALLINE WATERPROOFING | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of waterproofing, patching, and plugging material.
270 | 071616 | CRYSTALLINE WATERPROOFING | 1.5-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each product formulation, for tests performed by manufacturer and witnessed bya qualified testing agency.
271 | 071616 | CRYSTALLINE WATERPROOFING | 1.5-D | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
275 | 072726 | FLUID-APPLIED MEMBRANE AIR BARRIERS | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at. 1. Review air-barrier requirements and installation, special details, mockups, air-leakage and bond testing, air-barrier protection, and work scheduling that covers air barriers.
276 | 072726 | FLUID-APPLIED MEMBRANE AIR BARRIERS | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include manufacturer's written instructions for evaluating, preparing, and treating each substrate; technical data; dry film thickness; and tested physical and performance properties of products.
277 | 072726 | FLUID-APPLIED MEMBRANE AIR BARRIERS | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For air-barrier assemblies. 1. Show locations and extent of air-barrier materials, accessories, and assemblies specific to Project conditions. 2. Include details for substrate joints and cracks, counterflashing strips, penetrations, inside and outside corners, terminations, and tie-ins with adjoining construction. 3. Include details of interfaces with other materials that form part of air barrier.
278 | 072726 | FLUID-APPLIED MEMBRANE AIR BARRIERS | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
279 | 072726 | FLUID-APPLIED MEMBRANE AIR BARRIERS | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : From air-barrier manufacturer, certifying compatibility of air barriers and accessory materials with Project materials that connect to or that come in contact with the barrier.
280 | 072726 | FLUID-APPLIED MEMBRANE AIR BARRIERS | 1.6-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each air-barrier assembly, for tests performed bya qualified testing agency.
281 | 072726 | FLUID-APPLIED MEMBRANE AIR BARRIERS | 1.6-D | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
306 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.11-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of roofing system that fail in materials or workmanship within specified warranty period. 1. Special warranty includes roof membrane, base flashings, roof insulation, fasteners, cover boards, vapor retarder, substrate board, roof pavers, and other components of roofing system. 2. Warranty Period: 20 years from date of Substantial Completion.
290 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Roofing Conference : Conduct conference at Project site. 1. Meet with Owner, Architect, Construction Manager, Owner's insurer if applicable, testing and inspecting agency representative, roofing Installer, roofing system manufacturer's representative, deck Installer, air barrier Installer, and installers whose work interfaces with or affects roofing, including installers of roof accessories and roof-mounted equipment. 2. Review methods and procedures related to roofing installation, including manufacturer's written instructions. 3. Review and finalize construction schedule, and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays. 4. Examine deck substrate conditions and finishes for compliance with requirements, including flatness and fastening. 5. Review structural loading limitations of roof deck during and after roofing. 6. Review base flashings, special roofing details, roof drainage, roof penetrations, equipment curbs, and condition of other construction that affects roofing system. 7. Review governing regulations and requirements for insurance and certificates if applicable. 8. Review temporary protection requirements for roofing system during and after installation. 9. Review roof observation and repair procedures after roofing installation.
291 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. For insulation and roof system component fasteners, include copy of FM Approvals' RoofNav listing.
292 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include roof plans, sections, details, and attachments to other work, including the following: 1. Layout and thickness of insulation. 2. Base flashings and membrane termination details. 3. Flashing details at penetrations. 4. Tapered insulation layout, thickness, and slopes. 5. Roof plan showing orientation of steel roof deck and orientation of roof membrane, fastening spacings, and patterns for mechanically fastened roofing system. 6. Insulation fastening patterns for corner, perimeter, and field-of-roof locations. 7. Tie-in with adjoining air barrier.
293 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Verification : For the following products: 1. Roof membrane and flashings, of color required. 2. Walkway pads or rolls, of color required.
294 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.5-D | ACTION SUBMITTALS | Wind Uplift Resistance Submittal | Wind Uplift Resistance Submittal : For roofing system, indicating compliance with wind uplift performance requirements.
295 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer, manufacturer and testing agency.
296 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Manufacturer Certificates : - 1. Performance Requirement Certificate: Signed by roof membrane manufacturer, certifying that roofing system complies with requirements specified in "Performance Requirements" Article. a. Submit evidence of compliance with performance requirements. 2. Special Warranty Certificate: Signed by roof membrane manufacturer, certifying that all materials supplied under this Section are acceptable for special warranty.
297 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.6-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For roof membrane and insulation, for tests performed bya qualified testing agency, indicating compliance with specified requirements.
298 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.6-D | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For components of roofing system, from ICC-ES.
299 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.6-E | INFORMATIONAL SUBMITTALS | Test Reports | Field Test Reports : - 1. Concrete internal relative humidity test reports. 2. Fastener-pullout test results and manufacturer's revised requirements for fastener patterns.
300 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.6-F | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
301 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.6-G | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranties : For manufacturer's special warranties.
302 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.7-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For roofing system to include in maintenance manuals.
303 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 1.7-B | CLOSEOUT SUBMITTALS | Warranty | Certified statement from existing roof membrane manufacturer stating that existing roof warranty has not been affected by Work performed under this Section.
312 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 3.13-A | ROOFING INSTALLER'S WARRANTY | Warranty | WHEREAS _______________________________ of ___________________________, herein called the "Roofing Installer," has performed roofing and associated work ("work") on the following project: 1. Owner: 2. Address: 3. Building Name/Type: 4. Address: 5. Area of Work: 6. Acceptance Date: _________________. 7. Warranty Period: 8. Expiration Date: __________________.
313 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 3.13-B | ROOFING INSTALLER'S WARRANTY | Warranty | AND WHEREAS Roofing Installer has contracted (either directly with Owner or indirectly asa subcontractor) to warrant said work against leaks and faulty or defective materials and workmanship for designated Warranty Period,
314 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 3.13-C | ROOFING INSTALLER'S WARRANTY | Warranty | NOW THEREFORE Roofing Installer hereby warrants, subject to terms and conditions herein set forth, that during Warranty Period Roofing Installer will, at Roofing Installer's own cost and expense, make or cause to be made such repairs to or replacements of said work as are necessary to correct faulty and defective work and as are necessary to maintain said work ina watertight condition.
315 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 3.13-D | ROOFING INSTALLER'S WARRANTY | Warranty | This Warranty is made subject to the following terms and conditions : - 1. Specifically excluded from this Warranty are damages to work and other parts of the building, and to building contents, caused by: a. lightning; b. peak gust wind speed exceeding 115 mph; c. fire; d. failure of roofing system substrate, including cracking, settlement, excessive deflection, deterioration, and decomposition; e. faulty construction of parapet walls, copings, chimneys, skylights, vents, equipment supports, and other edge conditions and penetrations of the work; f. vapor condensation on bottom of roofing; and g. activity on roofing by others, including construction contractors, maintenance personnel, other persons, and animals, whether authorized or unauthorized by Owner. 2. When work has been damaged by any of foregoing causes, Warranty shall be null and void until such damage has been repaired by Roofing Installer and until cost and expense thereof have been paid by Owner or by another responsible party so designated. 3. Roofing Installer is responsible for damage to work covered by this Warranty but is not liable for consequential damages to building or building contents resulting from leaks or faults or defects of work. 4. During Warranty Period, if Owner allows alteration of work by anyone other than Roofing Installer, including cutting, patching, and maintenance in connection with penetrations, attachment of other work, and positioning of anything on roof, this Warranty shall become null and void on date of said alterations, but only to the extent said alterations affect work covered by this Warranty. If Owner engages Roofing Installer to perform said alterations, Warranty shall not become null and void unless Roofing Installer, before starting said work, shall have notified Owner in writing, showing reasonable cause for claim, that said alterations would likely damage or deteriorate work, thereby reasonably justifyinga limitation or termination of this Warranty. 5. During Warranty Period, if original use of roof is changed and it becomes used for, but was not originally specified for, a promenade, work deck, spray-cooled surface, flooded basin, or other use or service more severe than originally specified, this Warranty shall become null and void on date of said change, but only to the extent said change affects work covered by this Warranty. 6. Owner shall promptly notify Roofing Installer of observed, known, or suspected leaks, defects, or deterioration and shall afford reasonable opportunity for Roofing Installer to inspect work and to examine evidence of such leaks, defects, or deterioration. 7. This Warranty is recognized to be the only warranty of Roofing Installer on said work and shall not operate to restrict or cut off Owner from other remedies and resources lawfully available to Owner in cases of roofing failure. Specifically, this Warranty shall not operate to relieve Roofing Installer of responsibility for performance of original work according to requirements of the Contract Documents, regardless of whether Contract wasa contract directly with Owner ora subcontract with Owner's General Contractor.
316 | 075423 | THERMOPLASTIC-POLYOLEFIN (TPO) ROOFING | 3.13-E | ROOFING INSTALLER'S WARRANTY | Warranty | IN WITNESS THEREOF, this instrument has been duly executed this ___________ day of ___________________, ________________. 1. Authorized Signature: _______________________________________. 2. Name: ______________________________________. 3. Title: _______________________________________.
317 | 077200 | ROOF ACCESSORIES | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of roof accessory. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes.
318 | 077200 | ROOF ACCESSORIES | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For roof accessories. 1. Include plans, elevations, keyed details, and attachments to other work. Indicate dimensions, loadings, and special conditions. Distinguish between plant- and field- assembled work.
319 | 077200 | ROOF ACCESSORIES | 1.4-C | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color and texture specified, prepared on Samples of size to adequately show color.
320 | 077200 | ROOF ACCESSORIES | 1.4-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For roof curbs, equipment supports those indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation. 1. Detail mounting, securing, and flashing of roof-mounted items to roof structure. Indicate coordinating requirements with roof membrane system. 2. Wind-Restraint Details: Detail fabrication and attachment of wind restraints. Show anchorage details and indicate quantity, diameter, and depth of penetration of anchors.
321 | 077200 | ROOF ACCESSORIES | 1.5-A | INFORMATIONAL SUBMITTALS | Coordination Drawings | Coordination Drawings : Roof plans, drawn to scale, and coordinating penetrations and roof- mounted items. Show the following: 1. Size and location of roof accessories specified in this Section. 2. Method of attaching roof accessories to roof or building structure. 3. Other roof-mounted items including mechanical and electrical equipment, ductwork, piping, and conduit. (not being provided by equipment manufacturers) 4. Required clearances.
322 | 077200 | ROOF ACCESSORIES | 1.5-B | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranties : For manufacturer's special warranties.
323 | 077200 | ROOF ACCESSORIES | 1.6-A | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For roof accessories to include in operation and maintenance manuals.
324 | 077200 | ROOF ACCESSORIES | 1.7-A | WARRANTY | Special Warranty | Special Warranty on Painted Finishes : Manufacturer's standard form in which manufacturer agrees to repair finishes or replace roof accessories that show evidence of deterioration of factory-applied finishes within specified warranty period. 1. Fluoropolymer Finish: Deterioration includes, but is not limited to, the following: a. Color fading more than 5 Delta E units when tested according to ASTM D2244. b. Chalking in excess ofa No. 8 rating when tested according to ASTM D4214. c. Cracking, checking, peeling, or failure of paint to adhere to bare metal. 2. Finish Warranty Period: 10 years from date of Substantial Completion.
325 | 077200 | ROOF ACCESSORIES | 2.1-B | PERFORMANCE REQUIREMENTS | Delegated-Design Submittal | Delegated Design : Engagea qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design roof curbs and equipment supports to comply with wind performance requirements, including comprehensive engineering analysis bya qualified professional engineer, using performance requirements and design criteria indicated.
326 | 078100 | APPLIED FIRE PROTECTION | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Review products, design ratings, restrained and unrestrained conditions, densities, thicknesses, bond strengths, and other performance requirements.
327 | 078100 | APPLIED FIRE PROTECTION | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For the following: 1. Sprayed fire-resistive material. 2. Substrate primers. 3. Bonding agent. 4. Metal lath. 5. Reinforcing fabric. 6. Sealer. 7. Topcoat.
328 | 078100 | APPLIED FIRE PROTECTION | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Framing plans or schedules, or both, indicating the following: 1. Extent of fire protection for each construction and fire-resistance rating. 2. Applicable fire-resistance design designations ofa qualified testing and inspecting agency acceptable to authorities having jurisdiction. 3. Minimum sprayed fire-resistive material thicknesses needed to achieve required fire- resistance rating of each structural component and assembly. 4. Treatment of sprayed fire-resistive material after application.
329 | 078100 | APPLIED FIRE PROTECTION | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer and testing agency.
330 | 078100 | APPLIED FIRE PROTECTION | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of sprayed fire-resistive material.
331 | 078100 | APPLIED FIRE PROTECTION | 1.6-C | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For sprayed fire-resistive material, from ICC-ES.
332 | 078100 | APPLIED FIRE PROTECTION | 1.6-D | INFORMATIONAL SUBMITTALS | Test Reports | Preconstruction Test Reports : For fire protection.
333 | 078100 | APPLIED FIRE PROTECTION | 1.6-E | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
335 | 078100 | APPLIED FIRE PROTECTION | 3.3-K | APPLICATION | Mockups | Providea uniform finish complying with description indicated for each type of fire protection material and matching finish approved for required mockups.
340 | 078413 | PENETRATION FIRESTOPPING | 1.5-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
341 | 078413 | PENETRATION FIRESTOPPING | 1.6-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
342 | 078413 | PENETRATION FIRESTOPPING | 1.6-B | ACTION SUBMITTALS | Product Schedule | Product Schedule : For each penetration firestopping system. Include location, illustration of firestopping system, and design designation of qualified testing and inspecting agency. 1. Engineering Judgments: Where Project conditions require modification toa qualified testing and inspecting agency's illustration fora particular penetration firestopping system, submit illustration, with modifications marked, approved by penetration firestopping system manufacturer's fire-protection engineer as an engineering judgment or equivalent fire-resistance-rated assembly. Obtain approval of authorities having jurisdiction prior to submittal.
343 | 078413 | PENETRATION FIRESTOPPING | 1.7-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
344 | 078413 | PENETRATION FIRESTOPPING | 1.7-B | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each penetration firestopping system, for tests performed bya qualified testing agency.
345 | 078413 | PENETRATION FIRESTOPPING | 1.8-A | CLOSEOUT SUBMITTALS | Certificates | Installer Certificates : From Installer indicating that penetration firestopping systems have been installed in compliance with requirements and manufacturer's written instructions.
350 | 078443 | JOINT FIRESTOPPING | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
351 | 078443 | JOINT FIRESTOPPING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
352 | 078443 | JOINT FIRESTOPPING | 1.4-B | ACTION SUBMITTALS | Product Schedule | Product Schedule : For each joint firestopping system. Include location, illustration of firestopping system, and design designation of qualified testing agency. 1. Engineering Judgments: Where Project conditions require modification toa qualified testing agency's illustration fora particular joint firestopping system condition, submit illustration, with modifications marked, approved by joint firestopping system manufacturer's fire-protection engineer as an engineering judgment or equivalent fire- resistance-rated assembly.
353 | 078443 | JOINT FIRESTOPPING | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
354 | 078443 | JOINT FIRESTOPPING | 1.5-B | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each joint firestopping system, for tests performed bya qualified testing agency.
355 | 078443 | JOINT FIRESTOPPING | 1.6-A | CLOSEOUT SUBMITTALS | Certificates | Installer Certificates : From Installer indicating that joint firestopping systems have been installed in compliance with requirements and manufacturer's written instructions.
360 | 079200 | JOINT SEALANTS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each joint-sealant product.
361 | 079200 | JOINT SEALANTS | 1.3-B | ACTION SUBMITTALS | Samples | Samples for Initial Selection : Manufacturer's color charts consisting of strips of cured sealants showing the full range of colors available for each product exposed to view.
362 | 079200 | JOINT SEALANTS | 1.3-C | ACTION SUBMITTALS | Schedules | Joint-Sealant Schedule : Include the following information: 1. Joint-sealant application, joint location, and designation. 2. Joint-sealant manufacturer and product name. 3. Joint-sealant formulation. 4. Joint-sealant color.
363 | 079200 | JOINT SEALANTS | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For qualified testing agency.
364 | 079200 | JOINT SEALANTS | 1.4-B | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each kind of joint sealant, for tests performed bya qualified testing agency.
365 | 079200 | JOINT SEALANTS | 1.4-C | INFORMATIONAL SUBMITTALS | Schedules | Preconstruction Laboratory Test Schedule : Include the following information for each joint sealant and substrate material to be tested: 1. Joint-sealant location and designation. 2. Manufacturer and product name. 3. Type of substrate material. 4. Proposed test. 5. Number of samples required.
366 | 079200 | JOINT SEALANTS | 1.4-D | INFORMATIONAL SUBMITTALS | Test Reports | Preconstruction Laboratory Test Reports : From sealant manufacturer, indicating the following: 1. Materials forming joint substrates and joint-sealant backings have been tested for compatibility and adhesion with joint sealants. 2. Interpretation of test results and written recommendations for primers and substrate preparation are needed for adhesion.
367 | 079200 | JOINT SEALANTS | 1.4-E | INFORMATIONAL SUBMITTALS | Test Reports | Preconstruction Field-Adhesion-Test Reports : Indicate which sealants and joint preparation methods resulted in optimum adhesion to joint substrates based on testing specified in "Preconstruction Testing" Article.
368 | 079200 | JOINT SEALANTS | 1.4-F | INFORMATIONAL SUBMITTALS | Test Reports | Field-Adhesion-Test Reports : For each sealant application tested.
369 | 079200 | JOINT SEALANTS | 1.4-G | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranties : For special warranties.
372 | 079200 | JOINT SEALANTS | 1.5-C | QUALITY ASSURANCE | Mockups | Mockups : Install sealant in mockups of assemblies specified in other Sections that are indicated to receive joint sealants specified in this Section. Use materials and installation methods specified in this Section.
373 | 079200 | JOINT SEALANTS | 1.8-A | WARRANTY | Special Warranty | Special Installer's Warranty : Installer agrees to repair or replace joint sealants that do not comply with performance and other requirements specified in this Section within specified warranty period. 1. Warranty Period: Two years from date of Substantial Completion.
376 | 079200 | JOINT SEALANTS | 3.7-A | JOINT-SEALANT SCHEDULE | Schedules | Joint-Sealant Color : As selected by Architect from manufacturer's full range of colors. Exterior Building Joints, Horizontal and Vertical : 1. Metal to Metal: Type PS-1 2. Metal to Masonry: Type PS-1 3. Masonry to Masonry: Type PS-1 4. Threshold Setting Bed: Type PS-1 5. Masonry Expansion and Control Joints: Type SS-1 6. Glazing Sealant: Type SS-2 Sanitary Joints : 1. Walls to Plumbing Fixtures: Type SS-2 2. Counter Tops to Walls: Type SS-2 3. Pipe Penetrations: Type SS-2 4. Joints in ISO-8 or better spaces: Type SS-2 Interior Caulking : 1. Typical Narrow Joint (1/4 inch) or less at Walls and Adjacent Components: Types LS-1 2. Perimeter of Doors, Windows, which Adjoin Concrete or Masonry Surfaces: Types LS-1 3. Joints at Masonry Walls, Piers, Concrete Walls or Exterior Walls: Types LS-1 4. Wallboard Walls: Types LS-1
377 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for expansion joint cover assemblies.
378 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For each expansion joint cover assembly. 1. Include plans, elevations, sections, details, splices, block-out requirement, attachments to other work, and line diagrams showing entire route of each expansion joint. 2. Where expansion joint cover assemblies change planes, provide isometric or clearly detailed drawing depicting how components interconnect.
379 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.3-C | ACTION SUBMITTALS | Schedules | Expansion Joint Cover Assembly Schedule : Prepared by or under the supervision of the supplier. Include the following information in tabular form: 1. Manufacturer and model number for each expansion joint cover assembly. 2. Expansion joint cover assembly location cross-referenced to Drawings. 3. Nominal, minimum, and maximum joint width. 4. Movement direction. 5. Materials, colors, and finishes. 6. Product options. 7. Fire-resistance ratings.
380 | 079513.13 | INTERIOR EXPANSION JOINT COVER ASSEMBLIES | 1.4-A | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each fire-resistance-rated expansion joint cover assembly, for tests performed by manufacturer and witnessed bya qualified testing agency.
381 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.5-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
382 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.6-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, core descriptions, fire-resistance ratings and finishes.
383 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.6-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include the following: 1. Elevations of each door type. 2. Details of doors, including vertical- and horizontal-edge details and metal thicknesses. 3. Frame details for each frame type, including dimensioned profiles and metal thicknesses. 4. Locations of reinforcement and preparations for hardware. 5. Details of each different wall opening condition. 6. Details of electrical raceway and preparation for electrified hardware, access control systems, and security systems. 7. Details of anchorages, joints, field splices, and connections. 8. Details of accessories. 9. Details of moldings, removable stops, and glazing.
384 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.6-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For hollow-metal doors and frames with factory-applied color finishes. RFI 037 - Confirm Samples Required for DFH, Drywall, Toilet Acc, FP
385 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.6-D | ACTION SUBMITTALS | Samples | Samples for Verification : Cabinets_CLOSED
386 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.6-D-1 | ACTION SUBMITTALS | Samples | Finishes: For each type of exposed finish required, prepared on Samples of not less than 3 by 5 inches.
387 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.6-D-2 | ACTION SUBMITTALS | Fabrication | Fabrication: Prepare Samples approximately 12 by 12 inches to demonstrate compliance with requirements for quality of materials and construction: a. Doors: Show vertical-edge, top, and bottom construction; core construction; and hinge and other applied hardware reinforcement. Include separate section showing glazing if applicable. b. Frames: Show profile, corner joint, floor and wall anchors, and silencers. Include separate section showing fixed hollow-metal panels and glazing if applicable.
388 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.6-E | ACTION SUBMITTALS | Product Schedule | Product Schedule : For hollow-metal doors and frames, prepared by or under the supervision of supplier, using same reference numbers for details and openings as those on Drawings. Coordinate with final door hardware schedule.
389 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.7-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For door inspector. 1. Fire-Rated Door Inspector: Submit documentation of compliance with NFPA 80, Section 5.2.3.1. 2. Egress Door Inspector: Submit documentation of compliance with NFPA 101, Section 7.2.1.15.4. 3. Submit copy of DHI Fire and Egress Door Assembly Inspector (FDAI) certificate.
390 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.7-B | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each type of fire-rated hollow-metal door and frame assembly and thermally rated door assemblies for tests performed bya qualified testing agency indicating compliance with performance requirements.
391 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.7-C | INFORMATIONAL SUBMITTALS | Certifications | Oversize Construction Certification : For assemblies required to be fire-rated and exceeding limitations of labeled assemblies.
392 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.7-D | INFORMATIONAL SUBMITTALS | Reports | Field quality control reports.
393 | 081113 | HOLLOW METAL DOORS AND FRAMES | 1.8-A | CLOSEOUT SUBMITTALS | As-Builts | Record Documents : For fire-rated doors, list of door numbers and applicable room name and number to which door accesses.
401 | 083113 | ACCESS DOORS AND FRAMES | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, fire ratings, material descriptions, dimensions of individual components and profiles, and finishes.
402 | 083113 | ACCESS DOORS AND FRAMES | 1.4-B | ACTION SUBMITTALS | Product Schedule | Product Schedule : For access doors and frames.
403 | 083323 | OVERHEAD COILING DOORS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type and size of overhead coiling door and accessory. 1. Include construction details, material descriptions, dimensions of individual components, profiles for slats, and finishes. 2. Include rated capacities, operating characteristics, electrical characteristics, and furnished accessories. 3. Include description of automatic-closing device and testing and resetting instructions.
404 | 083323 | OVERHEAD COILING DOORS | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For each installation and for special components not dimensioned or detailed in manufacturer's product data. 1. Include plans, elevations, sections, and mounting details. 2. Include details of equipment assemblies, and indicate dimensions, required clearances, method of field assembly, components, and location and size of each field connection. 3. Include points of attachment and their corresponding static and dynamic loads imposed on structure. 4. For exterior components, include details of provisions for assembly expansion and contraction and for excluding and draining moisture to the exterior. 5. Show locations of controls, locking devices, and other accessories. 6. Include diagrams for power, signal, and control wiring.
405 | 083323 | OVERHEAD COILING DOORS | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : Manufacturer's finish charts showing full range of colors and textures available for units with factory-applied finishes. 1. Include similar Samples of accessories involving color selection.
406 | 083323 | OVERHEAD COILING DOORS | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
407 | 083323 | OVERHEAD COILING DOORS | 1.4-B | INFORMATIONAL SUBMITTALS | Certifications | Oversize Construction Certification : For door assemblies required to be fire-rated and that exceed size limitations of labeled assemblies.
408 | 083323 | OVERHEAD COILING DOORS | 1.4-C | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For special warranty.
409 | 083323 | OVERHEAD COILING DOORS | 1.5-A | CLOSEOUT SUBMITTALS | Special Warranty | Special warranty.
410 | 083323 | OVERHEAD COILING DOORS | 1.5-B | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For overhead coiling doors to include in maintenance manuals.
411 | 083323 | OVERHEAD COILING DOORS | 1.5-C | CLOSEOUT SUBMITTALS | As-Builts | Record Documents : For fire-rated doors, list of door numbers and applicable room name and number to which door accesses.
414 | 083323 | OVERHEAD COILING DOORS | 1.7-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of doors that fail in materials or workmanship within specified warranty period. 1. Warranty Period: Two years from date of Substantial Completion.
419 | 083323 | OVERHEAD COILING DOORS | 3.6-A | MAINTENANCE SERVICE | Maintenance Data | Initial Maintenance Service : Beginning at Substantial Completion, maintenance service shall include 12 months' full maintenance by skilled employees of coiling-door Installer. Include quarterly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper door operation. Parts and supplies shall be manufacturer's authorized replacement parts and supplies. 1. Perform maintenance, including emergency callback service, during normal working hours. 2. Include 24-hour-per-day, seven-day-per-week, emergency callback service.
420 | 083323 | OVERHEAD COILING DOORS | 3.7-A | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain overhead coiling doors.
445 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.10-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of aluminum-framed storefronts that do not comply with requirements or that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Structural failures, including, but not limited to, excessive deflection. b. Noise or vibration created by wind and thermal and structural movements. c. Deterioration of metals, metal finishes, and other materials beyond normal weathering. d. Water penetration through fixed glazing and framing areas. e. Failure of operating components. 2. Warranty Period: 10 years from date of Substantial Completion.
421 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site
422 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes.
423 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For aluminum-framed storefronts. Include plans, elevations, sections, full-size details, and attachments to other work. 1. Include details of provisions for assembly expansion and contraction and for draining moisture occurring within the assembly to the exterior. 2. Include full-size isometric details of each type of vertical-to-horizontal intersection of aluminum-framed storefronts, showing the following: a. Joinery, including concealed welds. b. Anchorage. c. Expansion provisions. d. Glazing. e. Flashing and drainage. 3. Show connection to and continuity with adjacent thermal, weather, air, and vapor barriers.
424 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For units with factory-applied color finishes.
425 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.5-D | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed finish required, in manufacturer's standard sizes.
426 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.5-E | ACTION SUBMITTALS | Samples | Fabrication Sample : Of each vertical-to-horizontal intersection of assemblies, made from 12- inch lengths of full-size components and showing details of the following: 1. Joinery, including concealed welds. 2. Anchorage. 3. Expansion provisions. 4. Glazing. 5. Flashing and drainage.
427 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.5-F | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For aluminum-framed storefronts indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
428 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-A | INFORMATIONAL SUBMITTALS | Mockups | Preconstruction Laboratory Mockup Testing Submittals : -
430 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-A-2 | INFORMATIONAL SUBMITTALS | Test Reports | Test Reports: Prepared bya qualified preconstruction testing agency for each mockup test.
431 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-A-3 | INFORMATIONAL SUBMITTALS | Drawings | Record Drawings: As-built drawings of preconstruction laboratory mockups showing changes made during preconstruction laboratory mockup testing.
432 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-B | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : - 1. For Installer and field testing agency. 2. For professional engineer's experience with providing delegated-design engineering services of the type indicated, including documentation that engineer is licensed in the jurisdiction in which Project is located.
433 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-C | INFORMATIONAL SUBMITTALS | Certificates | Energy Performance Certificates : For aluminum-framed storefronts, accessories, and components, from manufacturer. 1. Basis for Certification: NFRC-certified energy performance values for each aluminum- framed storefront.
434 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-D | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For aluminum-framed storefronts, for tests performed bya qualified testing agency.
435 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-E | INFORMATIONAL SUBMITTALS | Quality-Control Program | Quality-Control Program : Developed specifically for Project, including fabrication and installation, in accordance with recommendations in ASTM C1401. Include periodic quality- control reports.
436 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-F | INFORMATIONAL SUBMITTALS | Reports | Source quality-control reports.
437 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-G | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
438 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.6-H | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranties : For special warranties.
439 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.7-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For aluminum-framed storefronts to include in maintenance manuals.
440 | 084313 | ALUMINUM-FRAMED STOREFRONTS | 1.7-B | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data for Structural Sealant : For structural-sealant-glazed storefront to include in maintenance manuals. Include ASTM C1401 recommendations for post-installation-phase quality-control program.
470 | 087100 | DOOR HARDWARE | 1.12-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of door hardware that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Structural failures including excessive deflection, cracking, or breakage. b. Faulty operation of doors and door hardware. c. Deterioration of metals, metal finishes, and other materials beyond normal weathering and use. 2. Warranty Period: Three years from date of Substantial Completion unless otherwise indicated below: a. Electromagnetic Locks: Five years from date of Substantial Completion. b. Exit Devices: Two years from date of Substantial Completion. c. Manual Closers: 10 years from date of Substantial Completion.
451 | 087100 | DOOR HARDWARE | 1.5-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Conference participants shall include Installer's Architectural Hardware Consultant and Owner's security consultant.
452 | 087100 | DOOR HARDWARE | 1.5-B | PREINSTALLATION MEETINGS | Meetings | Keying Conference : Conduct conference at Project site. 1. Conference participants shall include Installer's Architectural Hardware Consultant and Owner's security consultant. 2. Incorporate conference decisions into keying schedule after reviewing door hardware keying system including, but not limited to, the following: a. Flow of traffic and degree of security required. b. Preliminary key system schematic diagram. c. Requirements for key control system. d. Requirements for access control. e. Address for delivery of keys.
453 | 087100 | DOOR HARDWARE | 1.6-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes.
454 | 087100 | DOOR HARDWARE | 1.6-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For electrified door hardware. 1. Include diagrams for power, signal, and control wiring. 2. Include details of interface of electrified door hardware and building safety and security systems.
455 | 087100 | DOOR HARDWARE | 1.6-C | ACTION SUBMITTALS | Samples | Samples : For each exposed product in each finish specified, in manufacturer's standard size. 1. Tag Samples with full product description to coordinate Samples with door hardware schedule.
456 | 087100 | DOOR HARDWARE | 1.6-D | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of exposed finish. RFI 037 - Confirm Samples Required for DFH, Drywall, Toilet Acc, FP Cabinets_CLOSED
457 | 087100 | DOOR HARDWARE | 1.6-E | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed product, in each finish specified. 1. Sample Size: Full-size units or minimum 2-by-4-inch Samples for sheet and 4-inch long Samples for other products. a. Full-size Samples will be returned to Contractor. Units that are acceptable and remain undamaged through submittal, review, and field comparison process may, after final check of operation, be incorporated into the Work, within limitations of keying requirements. 2. Tag Samples with full product description to coordinate Samples with door hardware schedule.
458 | 087100 | DOOR HARDWARE | 1.6-F | ACTION SUBMITTALS | Schedules | Door Hardware Schedule : Prepared by or under the supervision of Installer's Architectural Hardware Consultant. Coordinate door hardware schedule with doors, frames, and related work to ensure proper size, thickness, hand, function, and finish of door hardware. 1. Submittal Sequence: Submit door hardware schedule concurrent with submissions of Product Data, Samples, and Shop Drawings. Coordinate submission of door hardware schedule with scheduling requirements of other work to facilitate the fabrication of other work that is critical in Project construction schedule. 2. Format: Use same scheduling sequence and format and use same door numbers as in door hardware schedule in the Contract Documents. 3. Content: Include the following information: a. Identification number, location, hand, fire rating, size, and material of each door and frame. b. Locations of each door hardware set, cross-referenced to Drawings on floor plans and to door and frame schedule. c. Complete designations, including name and manufacturer, type, style, function, size, quantity, function, and finish of each door hardware product. d. Description of electrified door hardware sequences of operation and interfaces with other building control systems. e. Fastenings and other installation information. f. Explanation of abbreviations, symbols, and designations contained in door hardware schedule. g. Mounting locations for door hardware. h. List of related door devices specified in other Sections for each door and frame.
459 | 087100 | DOOR HARDWARE | 1.6-G | ACTION SUBMITTALS | Keying Schedule | Keying Schedule : Prepared by or under the supervision of Installer's Architectural Hardware Consultant, detailing Owner's final keying instructions for locks. Include schematic keying diagram and index each key set to unique door designations that are coordinated with the Contract Documents.
460 | 087100 | DOOR HARDWARE | 1.7-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer and Architectural Hardware Consultant.
461 | 087100 | DOOR HARDWARE | 1.7-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of electrified door hardware. 1. Certify that door hardware for use on each type and size of labeled fire-rated doors complies with listed fire-rated door assemblies.
462 | 087100 | DOOR HARDWARE | 1.7-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For compliance with accessibility requirements, for tests performed by manufacturer and witnessed bya qualified testing agency, for door hardware on doors located in accessible routes.
463 | 087100 | DOOR HARDWARE | 1.7-D | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
464 | 087100 | DOOR HARDWARE | 1.7-E | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For special warranty.
465 | 087100 | DOOR HARDWARE | 1.8-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For each type of door hardware to include in maintenance manuals.
466 | 087100 | DOOR HARDWARE | 1.8-B | CLOSEOUT SUBMITTALS | Schedules | Schedules : Final door hardware and keying schedule.
467 | 087100 | DOOR HARDWARE | 1.9-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Door Hardware: Two additional full assemblies for each type of hardware set. 2. Electrical Parts: Two additional full assemblies for each type of hardware set.
472 | 087100 | DOOR HARDWARE | 3.7-A | MAINTENANCE SERVICE | Maintenance Data | Maintenance Tools and Instructions : Furnisha complete set of specialized tools and maintenance instructions for Owner's continued adjustment, maintenance, and removal and replacement of door hardware.
473 | 087100 | DOOR HARDWARE | 3.7-B | MAINTENANCE SERVICE | Maintenance Data | Maintenance Service : Beginning at Substantial Completion, maintenance service shall include 12 months' full maintenance by skilled employees of door hardware Installer. Include quarterly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper door and door hardware operation. Parts and supplies shall be manufacturer's authorized replacement parts and supplies.
474 | 087100 | DOOR HARDWARE | 3.8-A | DEMONSTRATION | O&M Training And Demonstration | Train Owner's maintenance personnel to adjust, operate, and maintain door hardware.
490 | 088000 | GLAZING | 1.12-A | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty for Insulating Glass : Manufacturer agrees to replace insulating-glass units that deteriorate within specified warranty period. Deterioration of insulating glass is defined as failure of hermetic seal under normal use that is not attributed to glass breakage or to maintaining and cleaning insulating glass contrary to manufacturer's written instructions. Evidence of failure is obstruction of vision by dust, moisture, or film on interior surfaces of glass. 1. Warranty Period: 10 years from date of Substantial Completion.
491 | 088000 | GLAZING | 1.12-B | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty for Heat-Soaked Tempered Glass : Manufacturer agrees to replace heat-soaked tempered glass units that spontaneously break due to nickel sulfide (NiS) inclusions ata rate exceeding 0.3 percent (3/1000) within specified warranty period. Coverage for any other cause is excluded. 1. Warranty Period: 10 years from date of Substantial Completion.
475 | 088000 | GLAZING | 1.5-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays. 2. Review temporary protection requirements for glazing during and after installation.
476 | 088000 | GLAZING | 1.6-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
477 | 088000 | GLAZING | 1.6-B | ACTION SUBMITTALS | Samples | Glass Samples : For each type of the following products; 12 inches square. 1. Insulating glass.
478 | 088000 | GLAZING | 1.6-C | ACTION SUBMITTALS | Samples | Glazing Accessory Samples : For sealants, in 12-inch lengths.
479 | 088000 | GLAZING | 1.6-D | ACTION SUBMITTALS | Schedules | Glazing Schedule : List glass types and thicknesses for each size opening and location. Use same designations indicated on Drawings.
480 | 088000 | GLAZING | 1.6-E | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For glass indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by qualified professional engineer responsible for their preparation.
481 | 088000 | GLAZING | 1.7-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer, manufacturers of fabricated glass units, glass testing agency and sealant testing agency.
482 | 088000 | GLAZING | 1.7-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For glass.
483 | 088000 | GLAZING | 1.7-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For fabricated glass and glazing sealants, for tests performed bya qualified testing agency. 1. For glazing sealants, provide test reports based on testing current sealant formulations within previous 36-month period.
484 | 088000 | GLAZING | 1.7-D | INFORMATIONAL SUBMITTALS | Test Reports | Preconstruction adhesion and compatibility test report.
485 | 088000 | GLAZING | 1.7-E | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranties : For special warranties.
499 | 088813 | FIRE-RATED GLAZING | 1.10-A | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty for Tempered Glazing Units with Clear Intumescent Interlayer : - Manufacturer agrees to replace units that deteriorate within specified warranty period. Deterioration of tempered glazing units with clear intumenscent interlayer is defined as failure of hermetic seal under normal use that is not attributed to glass breakage or to maintaining and cleaning glass contrary to manufacturer's written instructions. Evidence of failure is air bubbles within units, or obstruction of vision by contamination or deterioration of intumescent interlayer. 1. Warranty Period: 10 years from date of Substantial Completion.
492 | 088813 | FIRE-RATED GLAZING | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
493 | 088813 | FIRE-RATED GLAZING | 1.5-B | ACTION SUBMITTALS | Samples | Glass Samples : For each type of glass product; 12 inches square.
494 | 088813 | FIRE-RATED GLAZING | 1.5-C | ACTION SUBMITTALS | Schedules | Glazing Schedule : List glass types and thicknesses for each size opening and location. Use same designations indicated on Drawings.
495 | 088813 | FIRE-RATED GLAZING | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer and glass testing agency.
496 | 088813 | FIRE-RATED GLAZING | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of glass and glazing product.
497 | 088813 | FIRE-RATED GLAZING | 1.6-C | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranties : For special warranties.
500 | 092116.23 | GYPSUM BOARD SHAFT WALL ASSEMBLIES | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each component of gypsum board shaft wall assembly.
501 | 092216 | NON-STRUCTURAL METAL FRAMING TO NONSTRUCTURAL FR | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
502 | 092216 | NON-STRUCTURAL METAL FRAMING TO NONSTRUCTURAL FR | 1.4-A | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of code-compliance certification for studs and tracks.
503 | 092216 | NON-STRUCTURAL METAL FRAMING TO NONSTRUCTURAL FR | 1.4-B | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For embossed, high-strength steel studs and tracks, firestop tracks and power-actuated fasteners, from ICC-ES or other qualified testing agency acceptable to authorities having jurisdiction.
505 | 092900 | GYPSUM BOARD | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For the following: 1. Gypsum wallboard. 2. Gypsum board, Type X. 3. Impact-resistant gypsum board. 4. Mold-resistant gypsum board. 5. Acoustically enhanced gypsum board. 6. Cementitious backer units. 7. Interior trim. 8. Joint treatment materials. 9. Sound-attenuation blankets. 10. Acoustical sealant.
506 | 092900 | GYPSUM BOARD | 1.3-B | ACTION SUBMITTALS | Samples | Samples : For the following products: RFI 037 - Samples Required for DFH, Drywall, Toilet Acc, FP Cabinets 1. Trim Accessories: Full-size Sample in 12-inch- long length for each trim accessory indicated.
507 | 092900 | GYPSUM BOARD | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Verification : For the following products: 1. Trim Accessories: Full-size Sample in 12-inch- long length for each trim accessory indicated.
508 | 093013 | CERAMIC TILING | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Review requirements in ANSI A108.01 for substrates and for preparation by other trades.
509 | 093013 | CERAMIC TILING | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
510 | 093013 | CERAMIC TILING | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Show locations of each type of tile and tile pattern. Show widths, details, and locations of expansion, contraction, control, and isolation joints in tile substrates and finished tile surfaces.
511 | 093013 | CERAMIC TILING | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Verification : - 1. Full-size units of each type and composition of tile and for each color and finish required. 2. Marble thresholds in 6-inch lengths.
512 | 093013 | CERAMIC TILING | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
513 | 093013 | CERAMIC TILING | 1.6-B | INFORMATIONAL SUBMITTALS | Certificates | Master Grade Certificates : For each shipment, type, and composition of tile, signed by tile manufacturer and Installer.
514 | 093013 | CERAMIC TILING | 1.6-C | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of product.
515 | 093013 | CERAMIC TILING | 1.6-D | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For tile-setting and -grouting products and certified porcelain tile.
516 | 093013 | CERAMIC TILING | 1.7-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match and are from same production runs as products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Tile and Trim Units: Furnish quantity of full-size units equal to 3 percent of amount installed for each type, composition, color, pattern, and size indicated. 2. Grout: Furnish quantity of grout equal to 3 percent of amount installed for each type, composition, and color indicated.
518 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
519 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
520 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.4-B | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color and texture specified, 6 inches in size.
521 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each component indicated and for each exposed finish required, prepared on Samples of sizes indicated below: 1. Acoustical Panels: Set of 6-inch- square Samples of each type, color, pattern, and texture. 2. Exposed Suspension-System Members, Moldings, and Trim: Set of 6-inch- long Samples of each type, finish, and color.
522 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.4-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For seismic restraints for ceiling systems. 1. Include design calculations for seismic restraints including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
523 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.5-A | INFORMATIONAL SUBMITTALS | Coordination Drawings | Coordination Drawings : Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved: 1. Ceiling suspension-system members. 2. Structural members to which suspension systems will be attached. 3. Method of attaching hangers to building structure. a. Furnish layouts for cast-in-place anchors, clips, and other ceiling attachment devices whose installation is specified in other Sections. 4. Carrying channels or other supplemental support for hanger-wire attachment where conditions do not permit installation of hanger wires at required spacing. 5. Size and location of initial access modules for acoustical panels. 6. Items penetrating finished ceiling and ceiling-mounted items including the following: a. Lighting fixtures. b. Diffusers. c. Grilles. d. Speakers. e. Sprinklers. f. Access panels. g. Perimeter moldings. h. Fire alarm devices. i. Lighting control / occupancy sensors 7. Show operation of hinged and sliding components covered by or adjacent to acoustical panels. 8. Minimum Drawing Scale: 1/4 inch = 1 foot.
524 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.5-B | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For testing agency.
525 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.5-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each acoustical panel ceiling, for tests performed by manufacturer and witnessed bya qualified testing agency.
526 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.5-D | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For each acoustical panel ceiling suspension system and anchor and fastener type, from ICC-ES.
527 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.5-E | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
528 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.6-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For finishes to include in maintenance manuals.
529 | 095113 | ACOUSTICAL PANEL CEILINGS | 1.7-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Acoustical Ceiling Units: Full-size panels equal to 2 percent of quantity installed. 2. Suspension-System Components: Quantity of each exposed component equal to 2 percent of quantity installed.
535 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
536 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.3-B | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color and texture specified, not less than 12 inches long.
537 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of product indicated and for each color, texture, and pattern required in manufacturer's standard-size Samples, but not less than 12 inches long.
538 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.3-D | ACTION SUBMITTALS | Product Schedule | Product Schedule : For resilient base and accessory products. Use same designations indicated on Drawings.
539 | 096513 | RESILIENT BASE AND ACCESSORIES | 1.4-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Furnish not less than 10 linear feet for every 500 linear feet or fraction thereof, of each type, color, pattern, and size of resilient product installed.
540 | 096516 | RESILIENT SHEET FLOORING | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
541 | 096516 | RESILIENT SHEET FLOORING | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For each type of resilient sheet flooring. 1. Include sheet flooring layouts, locations of seams, edges, columns, doorways, enclosing partitions, built-in furniture, cabinets, and cutouts. 2. Show details of special patterns.
542 | 096516 | RESILIENT SHEET FLOORING | 1.3-C | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color, texture, and pattern specified, in manufacturer's standard size, but not less than 6-by-9-inch sections. 1. For heat-welding bead, manufacturer's standard-size Samples, but not less than 9 inches long, of each color required.
543 | 096516 | RESILIENT SHEET FLOORING | 1.3-D | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of resilient sheet flooring, in manufacturer's standard size, but not less than 6-by-9-inch sections of each color, texture, and pattern required. 1. For heat-welding bead, manufacturer's standard-size Samples, but not less than 9 inches long, of each color required.
544 | 096516 | RESILIENT SHEET FLOORING | 1.3-E | ACTION SUBMITTALS | Samples | Welded-Seam Samples : For seamless-installation technique indicated and for each resilient sheet flooring product, color, and pattern required; with seam running lengthwise and in center of 6-by-9-inch Sample applied toa rigid backing and prepared by Installer for this Project.
545 | 096516 | RESILIENT SHEET FLOORING | 1.3-F | ACTION SUBMITTALS | Product Schedule | Product Schedule : For resilient sheet flooring. Use same designations indicated on Drawings.
546 | 096516 | RESILIENT SHEET FLOORING | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
547 | 096516 | RESILIENT SHEET FLOORING | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For each type of resilient sheet flooring to include in maintenance manuals.
548 | 096516 | RESILIENT SHEET FLOORING | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Resilient Sheet Flooring: Furnish not less than 10 linear feet for every 500 linear feet or fraction thereof, in roll form and in full roll width for each type, color, and pattern of flooring installed.
550 | 096519 | RESILIENT TILE FLOORING | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
551 | 096519 | RESILIENT TILE FLOORING | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For each type of resilient floor tile. 1. Include floor tile layouts, edges, columns, doorways, enclosing partitions, built-in furniture, cabinets, and cutouts. 2. Show details of special patterns.
552 | 096519 | RESILIENT TILE FLOORING | 1.3-C | ACTION SUBMITTALS | Samples | Samples : Full-size units of each color, texture, and pattern of floor tile required. 1. For heat-welding bead, manufacturer's standard-size Samples, but not less than 9 inches long, of each color required.
553 | 096519 | RESILIENT TILE FLOORING | 1.3-D | ACTION SUBMITTALS | Samples | Samples for Verification : Full-size units of each color and pattern of floor tile required. 1. For heat-welding bead, manufacturer's standard-size Samples, but not less than 9 inches long, of each color required.
554 | 096519 | RESILIENT TILE FLOORING | 1.3-E | ACTION SUBMITTALS | Product Schedule | Product Schedule : For floor tile. Use same designations indicated on Drawings.
555 | 096519 | RESILIENT TILE FLOORING | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
556 | 096519 | RESILIENT TILE FLOORING | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For each type of floor tile to include in maintenance manuals.
557 | 096519 | RESILIENT TILE FLOORING | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Floor Tile: Furnish one box for every 50 boxes or fraction thereof, of each type, color, and pattern of floor tile installed.
559 | 096566 | RESILIENT ATHLETIC FLOORING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
560 | 096566 | RESILIENT ATHLETIC FLOORING | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Show installation details and locations of the following: 1. Border tiles. 2. Floor patterns. 3. Layout, colors, widths, and dimensions of game lines and markers. 4. Locations of floor inserts for athletic equipment installed through flooring. 5. Seam locations for sheet flooring.
561 | 096566 | RESILIENT ATHLETIC FLOORING | 1.4-C | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each type, color, and pattern specified, 6-inch-square in size and of the same thickness indicated for the Work. 1. Game-Line- and Marker-Paint Samples: Include Sample sets showing game-line- and marker-paint colors applied to flooring. 2. Seam Samples: For each vinyl sheet flooring color and pattern required; with seam running lengthwise and in center of 6-by-9-inch Sample applied toa rigid backing and prepared by Installer for this Project.
562 | 096566 | RESILIENT ATHLETIC FLOORING | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For resilient athletic flooring to include in maintenance manuals.
563 | 096566 | RESILIENT ATHLETIC FLOORING | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Floor Tile: Furnish no fewer than 1 box for each 50 boxes or fraction thereof, of each type, color, pattern, and size of floor tile installed.
564 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Review methods and procedures related to terrazzo including, but not limited to, the following: a. Inspect and discuss condition of substrate and other preparatory work performed by other trades. b. Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays. c. Review special terrazzo designs and patterns.
565 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
566 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Include terrazzo installation requirements. Include plans, sections, component details, and relationship to other work. Show layout of the following: 1. Abrasive strips. 2. Stair treads, risers, and landings. 3. Precast terrazzo jointing and edge configurations. 4. Terrazzo patterns.
567 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.4-C | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color and texture specified, 6 inches in size.
568 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.4-D | ACTION SUBMITTALS | Samples | Samples for Verification : For each type, material, color, and pattern of terrazzo and accessory required showing the full range of color, texture, and pattern variations expected. Label each terrazzo Sample to identify manufacturer's matrix color and aggregate types, sizes, and proportions. Prepare Samples of same thickness and from same material to be used for the Work, in sizes indicated below: 1. Precast Terrazzo: 6-inch- square Samples. 2. Accessories: 6-inch- long Samples of each exposed strip item required.
569 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
570 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each type of terrazzo material or product.
571 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.5-C | INFORMATIONAL SUBMITTALS | Certificates | Installer Certificates : Signed by manufacturers certifying that installers comply with requirements.
573 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.6-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For terrazzo to include in maintenance manuals.
575 | 096623 | RESINOUS MATRIX TERRAZZO FLOORING | 1.7-B | QUALITY ASSURANCE | Mockups | Mockups : Build mockups to verify selections made under Sample submittals, to demonstrate aesthetic effects, and to set quality standards for materials and execution. 1. Build mockups for terrazzo including accessories. a. Include first three stair treads. 2. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.
589 | 096813 | TILE CARPETING | 1.11-A | WARRANTY | Special Warranty | Special Warranty for Carpet Tiles : Manufacturer agrees to repair or replace components of carpet tile installation that fail in materials or workmanship within specified warranty period. 1. Warranty does not include deterioration or failure of carpet tile due to unusual traffic, failure of substrate, vandalism, or abuse. 2. Failures include, but are not limited to, the following: a. More than 10 percent edge raveling, snags, and runs. b. Dimensional instability. c. Excess static discharge. d. Loss of tuft-bind strength. e. Loss of face fiber. f. Delamination. 3. Warranty Period: 10 years from date of Substantial Completion.
576 | 096813 | TILE CARPETING | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Review methods and procedures related to carpet tile installation including, but not limited to, the following: a. Review delivery, storage, and handling procedures. b. Review ambient conditions and ventilation procedures. c. Review subfloor preparation procedures.
577 | 096813 | TILE CARPETING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include manufacturer's written data on physical characteristics, durability, and fade resistance. 2. Include manufacturer's written installation recommendations for each type of substrate.
578 | 096813 | TILE CARPETING | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For carpet tile installation, plans showing the following: 1. Columns, doorways, enclosing walls or partitions, built-in cabinets, and locations where cutouts are required in carpet tiles. 2. Carpet tile type, color, and dye lot. 3. Type of subfloor. 4. Type of installation. 5. Pattern of installation. 6. Pattern type, location, and direction. 7. Pile direction. 8. Type, color, and location of insets and borders. 9. Type, color, and location of edge, transition, and other accessory strips. 10. Transition details to other flooring materials.
579 | 096813 | TILE CARPETING | 1.4-C | ACTION SUBMITTALS | Samples | Samples : For each of the following products and for each color and texture required. Label each Sample with manufacturer's name, material description, color, pattern, and designation indicated on Drawings and in schedules. 1. Carpet Tile: Full-size Sample. 2. Exposed Edge, Transition, and Other Accessory Stripping: 12-inch- long Samples.
580 | 096813 | TILE CARPETING | 1.4-D | ACTION SUBMITTALS | Samples | Samples for Verification : For each of the following products and for each color and texture required. Label each Sample with manufacturer's name, material description, color, pattern, and designation indicated on Drawings and in schedules. 1. Carpet Tile: Full-size Sample. 2. Exposed Edge, Transition, and Other Accessory Stripping: 12-inch- long Samples.
581 | 096813 | TILE CARPETING | 1.4-E | ACTION SUBMITTALS | Product Schedule | Product Schedule : For carpet tile. Use same designations indicated on Drawings.
582 | 096813 | TILE CARPETING | 1.4-F | ACTION SUBMITTALS | Certifications | Sustainable Product Certification : Provide ANSI/NSF 140 certification for carpet products.
583 | 096813 | TILE CARPETING | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
584 | 096813 | TILE CARPETING | 1.5-B | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For carpet tile, for tests performed bya qualified testing agency.
585 | 096813 | TILE CARPETING | 1.5-C | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For special warranty.
586 | 096813 | TILE CARPETING | 1.6-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For carpet tiles to include in maintenance manuals. Include the following: 1. Methods for maintaining carpet tile, including cleaning and stain-removal products and procedures and manufacturer's recommended maintenance schedule. 2. Precautions for cleaning materials and methods that could be detrimental to carpet tile.
587 | 096813 | TILE CARPETING | 1.7-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Carpet Tile: Full-size units equal to 5 percent of amount installed for each type indicated, but not less than 10 sq. yd..
590 | 097200 | WALL COVERINGS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include data on physical characteristics, durability, fade resistance, and fire-test-response characteristics.
591 | 097200 | WALL COVERINGS | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Show location and extent of each wall-covering type. Indicate pattern placement, seams, and termination points.
592 | 097200 | WALL COVERINGS | 1.3-C | ACTION SUBMITTALS | Samples | Samples : For each type of wall covering and for each color, pattern, texture, and finish specified, full width by 12 inches long in size. 1. Wall-Covering Sample: From same production run to be used for the Work.
593 | 097200 | WALL COVERINGS | 1.3-D | ACTION SUBMITTALS | Product Schedule | Product Schedule : For wall coverings. Use same designations indicated on Drawings.
594 | 097200 | WALL COVERINGS | 1.4-A | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each wall covering, for tests performed bya qualified testing agency.
595 | 097200 | WALL COVERINGS | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For wall coverings to include in maintenance manuals.
596 | 097200 | WALL COVERINGS | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same production run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Wall-Covering Materials: For each type, color, texture, and finish, full width by length to equal to 5 percent of amount installed.
597 | 097200 | WALL COVERINGS | 1.7-A | QUALITY ASSURANCE | Mockups | Mockups : Build mockups to verify selections made under Sample submittals and to demonstrate aesthetic effects and to set quality standards for installation. 1. Build mockups for each type of wall covering on each substrate required. Comply with requirements in ASTM F1141 for appearance shading characteristics. 2. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing. 3. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
610 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.12-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer and Installer agree to repair or replace components of stretched-fabric systems that fail in performance, materials, or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Acoustical performance. b. Fabric sagging, distorting, or releasing from panel edge. c. Warping of core. 2. Warranty Period: Two years from date of Substantial Completion.
598 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site
599 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include fabric facing, frame edge and trim, core material, and mounting indicated.
600 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For each stretched-fabric system. 1. Include plans, elevations, sections, and installation and system details. 2. Include details at head, base, joints, and corners; and details at ceiling, floor base, and wall intersections. Indicate frame-edge profile and core materials. 3. Include details at cutouts and penetrations for other work. 4. Include direction of fabric weave and pattern matching. 5. Show sewn-seam locations, types, and methods.
601 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Verification : For the following products: 1. Fabric: Full-width by approximately 12-inch long Sample, but not smaller than required to show complete pattern repeat, from dye lot to be used for the Work, and with specified treatments applied. Mark top and face of fabric. 2. Frame System: 12-inch-square Sample(s) showing each edge profile and corner. 3. Core Material: 12-inch-square Sample at corner. 4. Assembled System: Approximately 36 by 36 inches, including joints in mockup.
602 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.6-A | INFORMATIONAL SUBMITTALS | Coordination Drawings | Coordination Drawings : Elevations and other details, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved: 1. Electrical outlets, switches, and thermostats. 2. Items penetrating or covered by stretched-fabric systems include, but are not limited to the following: a. Lighting fixtures. b. Speakers. c. Alarms. d. Access panels. 3. Show operation of hinged and sliding components covered by or adjacent to stretched- fabric systems.
603 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.6-B | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
604 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.6-C | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of stretched-fabric system.
605 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.6-D | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For special warranty.
606 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.7-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For stretched-fabric systems to include in maintenance manuals. Include fabric manufacturer's written cleaning, stain-removal, restretching, and reupholstering instructions.
607 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.8-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Fabric: For each fabric, color, and pattern installed, furnish length equal to 10 percent of amount installed, but no fewer than 10 sq. yd., full width of bolt. 2. Framing and Related Installation Items: Furnish manufacturer's full-length units equal to 5 percent of amount installed, but no fewer than five units, including unopened adhesives.
609 | 097713 | STRETCHED-FABRIC WALL SYSTEMS | 1.9-B | QUALITY ASSURANCE | Mockups | Mockups : Build mockups to verify selections made under Sample submittals, to demonstrate aesthetic effects, and to set quality standards for materials, fabrication, and installation. 1. Build mockup of typical wall area as shown on Drawings. Include intersection of wall and ceiling, corners, and perimeters. 2. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing. 3. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
611 | 099113 | EXTERIOR PAINTING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. Include preparation requirements and application instructions. 1. Include printout of current "MPI Approved Products List" for each product category specified, with the proposed product highlighted. 2. Indicate VOC content.
612 | 099113 | EXTERIOR PAINTING | 1.4-B | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of paint system and each color and gloss of topcoat. 1. Submit Samples on rigid backing, 8 inches square. 2. Apply coats on Samples in steps to show each coat required for system. 3. Label each coat of each Sample. 4. Label each Sample for location and application area.
613 | 099113 | EXTERIOR PAINTING | 1.4-C | ACTION SUBMITTALS | Product Data | Product List : Cross-reference to paint system and locations of application areas. Use same designations indicated on Drawings and in schedules. Include color designations.
614 | 099113 | EXTERIOR PAINTING | 1.5-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Paint: 5 percent, but not less than 1 gal. of each material and color applied.
617 | 099123 | INTERIOR PAINTING | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. Include preparation requirements and application instructions. 1. Include Printout of current "MPI Approved Products List" for each product category specified, with the proposed product highlighted. 2. Indicate VOC content.
618 | 099123 | INTERIOR PAINTING | 1.4-B | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of paint system and in each color and gloss of topcoat. 1. Submit Samples on rigid backing, 8 inches square. 2. Apply coats on Samples in steps to show each coat required for system. 3. Label each coat of each Sample. 4. Label each Sample for location and application area.
619 | 099123 | INTERIOR PAINTING | 1.4-C | ACTION SUBMITTALS | Product Data | Product List : Cross-reference to paint system and locations of application areas. Use same designations indicated on Drawings and in schedules. Include color designations.
620 | 099123 | INTERIOR PAINTING | 1.5-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Paint: 5 percent, but not less than 1 gal. of each material and color applied.
623 | 099600 | HIGH-PERFORMANCE COATINGS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. Include preparation requirements and application instructions. 1. Include printout of current "MPI Approved Products List" for each product category specified, with the proposed product highlighted. 2. Indicate VOC content.
624 | 099600 | HIGH-PERFORMANCE COATINGS | 1.4-B | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of coating system and each color and gloss of topcoat indicated. 1. Submit Samples on rigid backing, 8 inches square. 2. Apply coats on Samples in steps to show each coat required for system. 3. Label each coat of each Sample. 4. Label each Sample for location and application area.
625 | 099600 | HIGH-PERFORMANCE COATINGS | 1.4-C | ACTION SUBMITTALS | Product Data | Product List : Cross-reference to coating system and locations of application areas. Use same designations indicated on Drawings and in schedules. Include color designations.
626 | 099600 | HIGH-PERFORMANCE COATINGS | 1.5-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Coatings: 5 percent, but not less than 1 gal. of each material and color applied.
629 | 099726 | CEMENTITIOUS COATINGS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
630 | 099726 | CEMENTITIOUS COATINGS | 1.3-B | ACTION SUBMITTALS | Samples | Samples for Verification : In each color and gloss of topcoat. 1. Submit Samples on rigid backing, not less than 8 inches square. 2. Apply coats on Samples in steps to show each coat required for system. 3. Label each coat of each Sample. 4. Label each Sample for location and application area.
631 | 099726 | CEMENTITIOUS COATINGS | 1.4-A | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each cementitious coating, from manufacturer.
632 | 099726 | CEMENTITIOUS COATINGS | 1.4-B | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : Based on evaluation of comprehensive tests performed by manufacturer and witnessed bya qualified testing agency or performed bya qualified testing agency, for each product formulation.
633 | 099726 | CEMENTITIOUS COATINGS | 1.5-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that are from same production run (batch mix) as materials applied and that are packaged with protective covering for storage and identified with labels describing contents. 1. Quantity: Furnish an additional 5 percent of each color applied.
635 | 102113.14 | STAINLESS-STEEL TOILET COMPARTMENTS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for toilet compartments.
636 | 102113.14 | STAINLESS-STEEL TOILET COMPARTMENTS | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For toilet compartments. 1. Include plans, elevations, sections, details, and attachment details. 2. Show locations of cutouts for compartment-mounted toilet accessories. 3. Show locations of reinforcements for compartment-mounted grab bars and locations of blocking for surface-mounted toilet accessories. 4. Show locations of centerlines of toilet fixtures. 5. Show locations of floor drains. 6. Show ceiling grid, ceiling-mounted items, and overhead support or bracing locations.
637 | 102113.14 | STAINLESS-STEEL TOILET COMPARTMENTS | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of toilet compartment material indicated. 1. Include Samples of hardware and accessories involving material and color selection.
638 | 102113.14 | STAINLESS-STEEL TOILET COMPARTMENTS | 1.3-D | ACTION SUBMITTALS | Samples | Samples for Verification : For the following products, in manufacturer's standard sizes unless otherwise indicated: 1. Each type of material, color, and finish required for toilet compartments, prepared on 6- inch-square Samples of same thickness and material indicated for Work. 2. Each type of hardware and accessory.
639 | 102113.14 | STAINLESS-STEEL TOILET COMPARTMENTS | 1.3-E | ACTION SUBMITTALS | Product Schedule | Product Schedule : For toilet compartments, prepared by or under the supervision of supplier, detailing location and selected colors for toilet compartment material.
640 | 102113.14 | STAINLESS-STEEL TOILET COMPARTMENTS | 1.4-A | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of toilet compartment.
641 | 102113.14 | STAINLESS-STEEL TOILET COMPARTMENTS | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For toilet compartments to include in maintenance manuals.
642 | 102113.14 | STAINLESS-STEEL TOILET COMPARTMENTS | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Door Hinges: Two hinges with associated fasteners. 2. Latch and Keeper: One latch and keeper with associated fasteners. 3. Door Bumper: Two door bumpers with associated fasteners. 4. Door Pull: One door pull with associated fasteners. 5. Fasteners: Ten fasteners of each size and type.
643 | 102213 | WIRE MESH PARTITIONS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
644 | 102213 | WIRE MESH PARTITIONS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, details, and attachments to other work. 2. Indicate clearances required for operation of doors.
645 | 102213 | WIRE MESH PARTITIONS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : 12-by-12-inch panel constructed of specified frame members and wire mesh. Show method of finishing members at intersections.
646 | 102213 | WIRE MESH PARTITIONS | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
647 | 102213 | WIRE MESH PARTITIONS | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
648 | 102213 | WIRE MESH PARTITIONS | 1.6-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For wire mesh partition hardware to include in maintenance manuals.
649 | 102213 | WIRE MESH PARTITIONS | 1.7-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Door Locks: Furnish 5 percent of quantity installed for each type indicated, but no fewer than locks.
652 | 102219 | DEMOUNTABLE PARTITIONS | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
653 | 102219 | DEMOUNTABLE PARTITIONS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
654 | 102219 | DEMOUNTABLE PARTITIONS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For demountable partitions. 1. Include plans, elevations, sections, and attachment details at floors, columns, permanent partitions, and ceilings; and method of erection and disassembly. 2. Include diagrams for power-, signal-, and control-wiring raceways; and details of access to raceways.
655 | 102219 | DEMOUNTABLE PARTITIONS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of the following products: 1. Face-Panel Finish: Manufacturer's standard-size unit, but not less than 6 inches square. 2. Linear Trim: 12-inch- long Samples. 3. Door Finish: Manufacturer's standard-size unit, but not less than 3 inches square. 4. Glazing: Manufacturer's standard-size unit, but not less than 3 inches square. 5. Hardware and Accessories: Whole units.
656 | 102219 | DEMOUNTABLE PARTITIONS | 1.5-A | INFORMATIONAL SUBMITTALS | Coordination Drawings | Coordination Drawings : Reflected ceiling plans and other details, drawn to scale, on which the following items are shown and coordinated with each other, using input from the installers of the items involved: 1. Suspended-ceiling components and dimensioned ceiling-grid layout. 2. Locations of fixed door and window mullions. 3. Overhead bracing, seismic restraints, and related structural members. 4. Ductwork above ceiling.
657 | 102219 | DEMOUNTABLE PARTITIONS | 1.5-B | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
658 | 102219 | DEMOUNTABLE PARTITIONS | 1.5-C | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of demountable partition.
659 | 102219 | DEMOUNTABLE PARTITIONS | 1.5-D | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each type of demountable-partition assembly, for tests performed by manufacturer and witnessed bya qualified testing agency.
660 | 102219 | DEMOUNTABLE PARTITIONS | 1.6-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For demountable partitions to include in maintenance manuals.
661 | 102219 | DEMOUNTABLE PARTITIONS | 1.6-B | CLOSEOUT SUBMITTALS | Qualification Data | Installer Qualifications : An entity that employs installers and supervisors who are trained and approved by manufacturer.
662 | 102219 | DEMOUNTABLE PARTITIONS | 1.6-C | CLOSEOUT SUBMITTALS | Mockups | Mockups : Build mockups to verify selections made under Sample submittals, to demonstrate aesthetic effects, and to set quality standards for fabrication and installation. 1. Build mockups for demountable partitions including accessories. a. Size: 48 inches by full height. b. Each type of exposed construction corner door and frame glass and frame and accessory panel. 2. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing. 3. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
663 | 102219 | DEMOUNTABLE PARTITIONS | 3.5-A | DEMONSTRATION | O&M Training And Demonstration | Train Owner's maintenance personnel to adjust, assemble, disassemble, and maintain demountable partitions.
664 | 102233 | ACCORDION FOLDING PARTITIONS | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
665 | 102233 | ACCORDION FOLDING PARTITIONS | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
666 | 102233 | ACCORDION FOLDING PARTITIONS | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For accordion folding partitions. 1. Include plans, elevations, sections, and attachment details. 2. Indicate storage and operating clearances. 3. Indicate location and installation requirements for hardware and track, blocking, and direction of travel. 4. Indicate facing-material seam locations if any. 5. Include diagrams for power, signal, and control wiring.
667 | 102233 | ACCORDION FOLDING PARTITIONS | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed material, facing material, and finish indicated, prepared on Samples of size indicated below: 1. Textile Facing Material: Full width by not less than 36-inch- long section of fabric from dye lot to be used for the Work, with specified treatments applied. Show complete pattern repeat. 2. Facing Material Other Than Textile: Manufacturer's standard-size unit, not less than 3 inches square. 3. Edge Material: Not less than full width by 3 inches long. 4. Hardware: Manufacturer's standard exposed door-operating device.
668 | 102233 | ACCORDION FOLDING PARTITIONS | 1.5-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For seismic bracing of accordion folding partitions. 1. Include design calculations for seismic restraints that brace tracks to structure above.
669 | 102233 | ACCORDION FOLDING PARTITIONS | 1.6-A | INFORMATIONAL SUBMITTALS | Coordination Drawings | Coordination Drawings : Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved: 1. Partition track, track supports and seismic bracing, switches, turning space, and storage layout. 2. Suspended ceiling components. 3. Structural members to which suspension systems will be attached. 4. Size and location of initial access modules for acoustical tile. 5. Items penetrating finished ceiling, including the following: a. Lighting fixtures. b. HVAC ductwork, outlets, and inlets. c. Speakers. d. Sprinklers. e. Smoke detectors.
670 | 102233 | ACCORDION FOLDING PARTITIONS | 1.6-B | INFORMATIONAL SUBMITTALS | Drawings | Setting Drawings : For embedded items and cutouts required in other work, including support- beam, mounting-hole template.
671 | 102233 | ACCORDION FOLDING PARTITIONS | 1.6-C | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
672 | 102233 | ACCORDION FOLDING PARTITIONS | 1.6-D | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of accordion folding partition, from manufacturer.
673 | 102233 | ACCORDION FOLDING PARTITIONS | 1.6-E | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each textile dye lot, signed by manufacturers.
674 | 102233 | ACCORDION FOLDING PARTITIONS | 1.6-F | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each accordion folding partition, for tests performed bya qualified testing agency.
675 | 102233 | ACCORDION FOLDING PARTITIONS | 1.6-G | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
676 | 102233 | ACCORDION FOLDING PARTITIONS | 1.6-H | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For manufacturer's special warranty.
677 | 102233 | ACCORDION FOLDING PARTITIONS | 1.7-A | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For accordion folding partitions to include in maintenance manuals. 1. In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following: a. Facing materials and finishes for exposed trim and accessories. Include precautions for cleaning materials and methods that could be detrimental to finishes and performance. b. Seals, hardware, track, carriers, and other operating components. c. Electric operator and controls.
678 | 102233 | ACCORDION FOLDING PARTITIONS | 1.7-B | CLOSEOUT SUBMITTALS | Qualification Data | Installer Qualifications : An entity that employs installers and supervisors who are trained and approved by manufacturer.
679 | 102233 | ACCORDION FOLDING PARTITIONS | 1.8-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of accordion folding partitions that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Faulty operation of accordion folding partitions. b. Deterioration of metals, metal finishes, and other materials beyond normal use. 2. Warranty Period: Five years from date of Substantial Completion. 3. Warranty Period for Pantographic Frames, Trolleys, and Tracks: 10 years from date of Substantial Completion.
680 | 102233 | ACCORDION FOLDING PARTITIONS | 3.4-A | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain accordion folding partitions.
681 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.4-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
682 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
683 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For operable glass-panel partitions. 1. Include plans, elevations, sections, details, numbered panel installation sequence, and attachments to other work. 2. Indicate stacking and operating clearances. Indicate location and installation requirements for hardware and track, blocking, and direction of travel.
684 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.5-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed material, finish, covering, or facing, prepared on Samples of size indicated below: 1. Panel Edge Material: Not less than 3 inches long. 2. Glass: Units 12 inches square. 3. Hardware: One of each exposed door-operating device.
685 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.5-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For operable glass-panel partitions. 1. Include design calculations for seismic restraints that brace tracks to structure above.
686 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.6-A | INFORMATIONAL SUBMITTALS | Coordination Drawings | Coordination Drawings : Reflected ceiling plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved: 1. Partition track, track supports and bracing, switches, turning space, and storage layout. 2. Suspended ceiling components. 3. Structural members to which suspension systems are attached. 4. Size and location of initial access modules for acoustical tile. 5. Items penetrating finished ceiling, including the following: a. Lighting fixtures. b. HVAC ductwork, outlets, and inlets. c. Speakers. d. Sprinklers. e. Smoke detectors. f. Access panels. 6. Plenum acoustical barriers.
687 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.6-B | INFORMATIONAL SUBMITTALS | Drawings | Setting Drawings : For embedded items and cutouts required in other work, including support- beam, mounting-hole template.
688 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.6-C | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For qualified Installer.
689 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.6-D | INFORMATIONAL SUBMITTALS | Certificates | Seismic Qualification Certificates : For operable glass-panel partitions, tracks, accessories, and components, from manufacturer. Include seismic capacity of partition assemblies to remain in vertical position duringa seismic event and the following: 1. Basis for Certification: Indicate whether certification is based on analysis, testing, or experience data, according to ASCE/SEI 7. 2. Detailed description of partition anchorage devices on which the certification is based and their installation requirements.
690 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.6-E | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of operable glass-panel partition.
691 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.6-F | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each operable glass-panel partition, for tests performed bya qualified testing agency.
692 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.6-G | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For manufacturer's special warranty.
693 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.7-A | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For operable glass-panel partitions to include in maintenance manuals. 1. In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following: a. Panel finish and finishes for exposed trim and accessories. Include precautions for cleaning materials and methods that could be detrimental to finishes and performance. b. Seals, hardware, track, track switches, carriers, and other operating components.
694 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.7-B | CLOSEOUT SUBMITTALS | Qualification Data | Installer Qualifications : An entity that employs installers and supervisors who are trained and approved by manufacturer.
695 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 1.9-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of operable glass-panel partitions that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Faulty operation of operable glass-panel partitions. b. Deterioration of metals, metal finishes, and other materials beyond normal use. 2. Warranty Period: Two years from date of Substantial Completion.
696 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 3.4-A | MAINTENANCE SERVICE | Maintenance Data | Maintenance Service : Beginning at Substantial Completion, maintenance service shall include 12 months' full maintenance by manufacturer's authorized service representative. Include quarterly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper operable-partition operation. Parts and supplies shall be manufacturer's authorized replacement parts and supplies.
697 | 102239.13 | FOLDING GLASS-PANEL PARTITIONS | 3.5-A | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain operable glass-panel partitions.
698 | 102600 | WALL AND DOOR PROTECTION | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, impact strength, dimensions of individual components and profiles, and finishes. 2. Include fire ratings of units recessed in fire-rated walls and listings for door-protection items attached to fire-rated doors.
699 | 102600 | WALL AND DOOR PROTECTION | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For each type of wall and door protection showing locations and extent. 1. Include plans, elevations, sections, and attachment details.
700 | 102600 | WALL AND DOOR PROTECTION | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed finish on the following products, prepared on Samples of size indicated below: 1. Wall Guards: 12 inches long. Include examples of joinery, corners, end caps, top caps, and field splices. Corner Guards: 12 inches long. Include example top caps.
701 | 102600 | WALL AND DOOR PROTECTION | 1.4-A | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of handrail.
702 | 102600 | WALL AND DOOR PROTECTION | 1.4-B | INFORMATIONAL SUBMITTALS | Certificates | Material Certificates : For each type of exposed plastic material.
703 | 102600 | WALL AND DOOR PROTECTION | 1.4-C | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For special warranty.
704 | 102600 | WALL AND DOOR PROTECTION | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For each type of wall and door protection product to include in maintenance manuals. 1. Include recommended methods and frequency of maintenance for maintaining best condition of plastic covers under anticipated traffic and use conditions. Include precautions against using cleaning materials and methods that may be detrimental to finishes and performance.
705 | 102600 | WALL AND DOOR PROTECTION | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials, from the same product run, that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Wall-Guard Covers: Full-size plastic covers of maximum length equal to 2 percent of each type, color, and texture of cover installed, but no fewer than two, 96-inch- long units. 2. Corner-Guard Covers: Full-size plastic covers of maximum length equal to 2 percent of each type, color, and texture of cover installed, but no fewer than two, 48-inch- long units. 3. Mounting and Accessory Components: Amounts proportional to the quantities of extra materials. Package mounting and accessory components with each extra material.
706 | 102600 | WALL AND DOOR PROTECTION | 1.8-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of wall- and door- protection units that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Structural failures including detachment of components from each other or from the substrates, delamination, and permanent deformation beyond normal use. b. Deterioration of metals, metal finishes, plastics, and other materials beyond normal use. 2. Warranty Period: Five years from date of Substantial Completion.
707 | 102800 | TOILET, BATH, AND LAUNDRY ACCESSORIES | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes. 2. Include anchoring and mounting requirements, including requirements for cutouts in other work and substrate preparation. 3. Include electrical characteristics.
708 | 102800 | TOILET, BATH, AND LAUNDRY ACCESSORIES | 1.5-B | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each finish specified, full size. Project No. 184043 102800 - 1 of 6 Toilet, Bath, and Laundry Accessories Rev. 0, 08MAY20 RFI 037 - Co nfirm Samples Required for DFH, Issued for Construction Drywall, Toilet Acc, FP Cabinets_CLOSED 1. Approved full-size Samples will be returned and may be used in the Work.
709 | 102800 | TOILET, BATH, AND LAUNDRY ACCESSORIES | 1.5-C | ACTION SUBMITTALS | Product Schedule | Product Schedule : Indicating types, quantities, sizes, and installation locations by room of each accessory required. 1. Identify locations using room designations indicated. 2. Identify accessories using designations indicated.
710 | 102800 | TOILET, BATH, AND LAUNDRY ACCESSORIES | 1.5-D | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For grab bars. 1. Include structural design calculations indicating compliance with specified structural- performance requirements.
711 | 102800 | TOILET, BATH, AND LAUNDRY ACCESSORIES | 1.6-A | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For manufacturer's special warranties.
712 | 102800 | TOILET, BATH, AND LAUNDRY ACCESSORIES | 1.7-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For accessories to include in maintenance manuals.
713 | 102800 | TOILET, BATH, AND LAUNDRY ACCESSORIES | 1.8-A | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty for Mirrors : Manufacturer agrees to repair or replace mirrors that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, visible silver spoilage defects. 2. Warranty Period: 10 years from date of Substantial Completion.
714 | 104413 | FIRE PROTECTION CABINETS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Show door hardware, cabinet type, trim style, and panel style. Include roughing-in dimensions and details showing recessed-mounting method and relationships of box and trim to surrounding construction.
715 | 104413 | FIRE PROTECTION CABINETS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For fire-protection cabinets. 1. Include plans, elevations, sections, details, and attachments to other work. RFI 037 - Samples Required for DFH,
716 | 104413 | FIRE PROTECTION CABINETS | 1.4-C | ACTION SUBMITTALS | Samples | Samples : For each type of exposed finish required. Drywall, Toilet Acc, FP Cabinets
717 | 104413 | FIRE PROTECTION CABINETS | 1.4-D | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of exposed finish required.
718 | 104413 | FIRE PROTECTION CABINETS | 1.4-E | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of exposed finish required, prepared on samples 6 by 6 inches square.
719 | 104413 | FIRE PROTECTION CABINETS | 1.4-F | ACTION SUBMITTALS | Product Schedule | Product Schedule : For fire-protection cabinets. Coordinate final fire-protection cabinet schedule with fire-extinguisher schedule to ensure proper fit and function.
720 | 104413 | FIRE PROTECTION CABINETS | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For fire-protection cabinets to include in maintenance manuals.
721 | 104416 | FIRE EXTINGUISHERS | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Review methods and procedures related to fire extinguishers including, but not limited to, the following: a. Schedules and coordination requirements.
722 | 104416 | FIRE EXTINGUISHERS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. Include rating and classification, material descriptions, dimensions of individual components and profiles, and finishes for fire extinguisher.
723 | 104416 | FIRE EXTINGUISHERS | 1.4-B | ACTION SUBMITTALS | Product Schedule | Product Schedule : For fire extinguishers. Coordinate final fire-extinguisher schedule with fire- protection cabinet schedule to ensure proper fit and function.
724 | 104416 | FIRE EXTINGUISHERS | 1.5-A | INFORMATIONAL SUBMITTALS | Warranty | Warranty : Sample of special warranty.
725 | 104416 | FIRE EXTINGUISHERS | 1.6-A | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For fire extinguishers to include in maintenance manuals.
726 | 104416 | FIRE EXTINGUISHERS | 1.8-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer's standard form in which manufacturer agrees to repair or replace fire extinguishers that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Failure of hydrostatic test according to NFPA 10 when testing interval required by NFPA 10 is within the warranty period. b. Faulty operation of valves or release levers. 2. Warranty Period: Six years from date of Substantial Completion.
735 | 105123 | PLASTIC-LAMINATE-CLAD LOCKERS | 1.10-A | WARRANTY | Special Warranty | Special Warranty : Manufacturer agrees to repair or replace components of lockers that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Structural failures. b. Faulty operation of locks or hardware. c. Deterioration of wood, finishes, and other materials beyond normal use. 2. Warranty Period: Three years from date of Substantial Completion.
727 | 105123 | PLASTIC-LAMINATE-CLAD LOCKERS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for each type of locker and bench.
728 | 105123 | PLASTIC-LAMINATE-CLAD LOCKERS | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For plastic-laminate-clad wood lockers. 1. Include plans, elevations, sections, and attachment details. 2. Show details full size. 3. Show locations and sizes of furring, blocking, and hanging strips, including concealed blocking and reinforcement specified in other Sections. 4. Show locations and sizes of cutouts and holes for items installed in lockers. 5. Show locker fillers, trim, base, sloping tops, and accessories. 6. Show locker identification system and numbering sequence.
729 | 105123 | PLASTIC-LAMINATE-CLAD LOCKERS | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of the following: 1. High-pressure decorative laminates. 2. Thermoset decorative overlay panels. 3. Carpet.
730 | 105123 | PLASTIC-LAMINATE-CLAD LOCKERS | 1.3-D | ACTION SUBMITTALS | Samples | Samples for Verification : For the following products: 1. Plastic-laminate-clad panels, not less than 8 by 10 inches, for each type, color, pattern, and surface finish, with separate samples of unfaced panel product used for core. 2. Thermoset decorative-overlay-surfaced panels, not less than 8 by 10 inches, for each type, color, pattern, and surface finish. 3. Corner pieces of locker front frame joints between stiles and rail, as well as exposed end pieces, not less than 18 inches wide by 18 inches high by 6 inches deep. 4. Exposed cabinet hardware and accessories, one unit for each type and finish. 5. Carpet, not less than 8 by 10 inches, for each type, color, and pattern.
731 | 105123 | PLASTIC-LAMINATE-CLAD LOCKERS | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
732 | 105123 | PLASTIC-LAMINATE-CLAD LOCKERS | 1.4-B | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For special warranty.
733 | 105123 | PLASTIC-LAMINATE-CLAD LOCKERS | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For adjusting, repairing, and replacing locker doors and latching mechanisms to include in maintenance manuals.
734 | 105123 | PLASTIC-LAMINATE-CLAD LOCKERS | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Locker doors, complete with specified door hardware. Furnish no fewer than five doors of each type and color installed. 2. Units of the following locker hardware items equal to 10 percent of amount installed for each type and finish installed, but no fewer than five units: a. Hinges. b. Pulls. c. Shelf rests. d. Cylinder locks. e. Hooks.
736 | 107300 | PRE-ENGINEERED CANOPY SYSTEM | 1.2-A | SUBMITTALS | Product Data | Submit manufacturers product data. Include construction details, material descriptions, profiles and finishes of components.
737 | 107300 | PRE-ENGINEERED CANOPY SYSTEM | 1.2-B | SUBMITTALS | Shop Drawings | Submit shop drawings. Include plans, elevations, and details.
738 | 107300 | PRE-ENGINEERED CANOPY SYSTEM | 1.2-C | SUBMITTALS | Samples | Submit manufacturers color charts showing the full range of colors available for factory finished aluminum. 1. When requested, submit samples for each exposed finish required, in same thickness and material indicated for the work and in size indicated below. If finishes involve normal color variations, include sample sets consisting of two or more units showing the full range of variations expected. a. Sandwich panels: 7x12 units b. Factory finished aluminum: 5 long sections
739 | 107300 | PRE-ENGINEERED CANOPY SYSTEM | 1.2-D | SUBMITTALS | Certificates | Submit Installer Certificate, signed by installer, certifying compliance with project qualification requirements.
740 | 107300 | PRE-ENGINEERED CANOPY SYSTEM | 1.2-E | SUBMITTALS | Performance Data | Submit product reports froma qualified independent testing agency indicating each type and class of panel system complies with the project performance requirements, based on comprehensive testing of current products. Previously completed reports will be acceptable if for current manufacturer and indicative of products used on this project. 1. Reports required (if applicable) are: a. International Building Code Evaluation Report (AC 177) b. Flame Spread and Smoke Developed (UL 723) Submit UL Card c. Burn Extent (ASTM D 635) d. Color Difference (ASTM D 2244) e. Impact Strength (UL 972) f. Bond Tensile Strength (ASTM C 297 after aging by ASTM D 1037) g. Bond Shear Strength (ASTM D 1002) h. Beam Bending Strength (ASTM E 72) i. Insulation U-Factor (NFRC 100 or ASTM C-236) j. 1200F Fire Resistance (SWRI) k. Fall Through Resistance (ASTM E 661) l. Class A Roof Covering Burning Brand (ASTM E 108)
741 | 107300 | PRE-ENGINEERED CANOPY SYSTEM | 1.2-F | SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For pre-engineered canopy system.
742 | 107300 | PRE-ENGINEERED CANOPY SYSTEM | 1.3-A | CLOSEOUT SUBMITTALS | Maintenance Data | Provide project maintenance manuals.
745 | 107300 | PRE-ENGINEERED CANOPY SYSTEM | 1.5-C | PERFORMANCE REQUIREMENTS | Delegated-Design Submittal | Delegated Design : Engagea qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design complete canopy system framing and anchorage. 1. Include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
746 | 107300 | PRE-ENGINEERED CANOPY SYSTEM | 1.7-A | WARRANTY | Warranty | Provide manufacturer's and installer's written warranty agreeing to repair or replace canopy system work, which fails in materials or workmanship within five year from the date of delivery. Failure of materials or workmanship shall include leakage, excessive deflection, deterioration of finish on metal in excess of normal weathering, defects in accessories, insulated translucent sandwich panels and other components of the work.
747 | 111316 | LOADING DOCK SEALS AND SHELTERS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes. 2. Include electrical characteristics of inflatable blower motor.
748 | 111316 | LOADING DOCK SEALS AND SHELTERS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - 1. Include plans, elevations, sections, and attachment details. 2. Detail assemblies and indicate dimensions, weights, required clearances, method of field assembly, components, and location and size of anchors and field connection. 3. Include diagrams for power, signal, and control wiring of inflatable blower motor.
749 | 111316 | LOADING DOCK SEALS AND SHELTERS | 1.4-C | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of fabric indicated.
750 | 111316 | LOADING DOCK SEALS AND SHELTERS | 1.5-A | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For inflatable units to include in operation and maintenance manuals.
761 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 1.11-A | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty : Manufacturer agrees to repair or replace dock levelers that fail in materials or workmanship within specified warranty period. 1. Failures include, but are not limited to, the following: a. Structural failures including cracked or broken structural support members, load- bearing welds, and front and rear hinges. b. Faulty operation of operators, control system, or hardware. c. Deck plate failures including cracked plate or permanent deformation in excess of 1/4 inch between deck supports. d. Hydraulic system failures including failure of hydraulic seals and cylinders. 2. Warranty Period for Structural Assembly: 10 years from date of Substantial Completion. 3. Warranty Period for Hydraulic System: Five years from date of Substantial Completion. 4. Warranty shall be for unlimited usage of leveler for the specified rated capacity over the term of the warranty.
751 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 1.5-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Inspect and discuss electrical roughing-in, equipment bases, and other preparatory work specified elsewhere. 2. Review sequence of operation for each type of loading dock equipment. 3. Review coordination of interlocked equipment specified in this Section and elsewhere. 4. Review required testing, inspecting, and certifying procedures.
752 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 1.6-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for stationary loading dock equipment. 2. Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.
753 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 1.6-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For stationary loading dock equipment. 1. Include plans, elevations, sections, and attachment details. 2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of anchors and each field connection. 3. Include diagrams for power, signal, and control wiring.
754 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 1.7-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
755 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 1.7-B | INFORMATIONAL SUBMITTALS | Certificates | Welding certificates.
756 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 1.7-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each dock leveler, for tests performed by manufacturer and witnessed bya qualified testing agency. 1. Indicate compliance of dock levelers with requirements in MH 30.1 for determining rated capacity based on comprehensive testing within last two years of current products. 2. Submittal Form: According to MH 30.1.
757 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 1.7-D | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For manufacturer's special warranty.
758 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 1.8-A | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For stationary loading dock equipment to include in operation and maintenance manuals.
762 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 3.6-A | MAINTENANCE SERVICE | Maintenance Data | Beginning at Substantial Completion, maintenance service shall include 12 months' full maintenance by skilled employees of loading dock equipment Installer. Include preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper loading dock equipment operation at rated speed and capacity. Parts and supplies shall be manufacturer's authorized replacement parts and supplies.
763 | 111319 | STATIONARY LOADING DOCK EQUIPMENT | 3.7-A | DEMONSTRATION | O&M Training And Demonstration | Train Owner's maintenance personnel to adjust, operate, and maintain loading dock equipment.
764 | 115313 | LABORATORY FUME HOODS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
765 | 115313 | LABORATORY FUME HOODS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For laboratory fume hoods. 1. Include plans, elevations, sections, and attachment details. 2. Indicate details for anchoring fume hoods to permanent building construction including locations of blocking and other supports. Include calculations demonstrating that anchorages comply with seismic performance requirements. 3. Indicate locations and types of service fittings together with associated service supply connection required. 4. Indicate duct connections, electrical connections, and locations of access panels. 5. Include roughing-in information for mechanical, plumbing, and electrical connections. 6. Show adjacent walls, doors, windows, other building components, laboratory casework, and other laboratory equipment. Indicate clearances from the above items. 7. Include layout of fume hoods in relation to lighting fixtures and air-conditioning registers and grilles. 8. Include coordinated dimensions for laboratory equipment specified in other Sections.
766 | 115313 | LABORATORY FUME HOODS | 1.4-C | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For fume hoods indicated to comply with seismic performance requirements and design criteria.
767 | 115313 | LABORATORY FUME HOODS | 1.5-A | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : Showing compliance with specified performance requirements for as- manufactured containment and static pressure loss, based on evaluation of comprehensive tests performed by manufacturer and witnessed bya qualified testing agency.
768 | 115313 | LABORATORY FUME HOODS | 1.5-B | INFORMATIONAL SUBMITTALS | Reports | Source quality-control reports.
769 | 115313 | LABORATORY FUME HOODS | 1.5-C | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
770 | 115313 | LABORATORY FUME HOODS | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish complete touchup kit for each type and color of fume hood finish provided. Include fillers, primers, paints, and other materials necessary to perform permanent repairs to damaged fume hood finish.
771 | 115313 | LABORATORY FUME HOODS | 2.9-A | SOURCE QUALITY CONTROL | O&M Training And Demonstration | Demonstrate fume hood performance before shipment by testing fume hoods according to ASHRAE 110 as modified in "Performance Requirements" Article. Provide testing facility, instruments, equipment, and materials needed for tests.
774 | 118226 | FACILITY WASTE COMPACTORS | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site. 1. Inspect and discuss electrical, plumbing, and sprinkler roughing-in; equipment bases; and other preparatory work specified elsewhere. 2. Review coordination of chute and diverter locations with waste compactors. 3. Review sanitary requirements for water bibs, floor drains, and grease traps if required for Project to reduce decomposition and odors. 4. Review haul routes of waste to the compactor, route of hauler's equipment, and protections along these routes that are specified elsewhere. 5. Review required testing, inspection, and certification procedures.
775 | 118226 | FACILITY WASTE COMPACTORS | 1.4-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include rated capacities, operating characteristics, furnished specialties and accessories, and finishes.
776 | 118226 | FACILITY WASTE COMPACTORS | 1.4-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For each waste compactor and for special components not dimensioned or detailed in manufacturer's product data. 1. Include plans, elevations, sections, and attachment details. 2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection. 3. Dimension chute and diverter locations that interface with waste compactors. 4. Include location and installation details of automatic sprinkler in hopper of each chute- fed compactor. 5. Indicate equipment access points and required space for equipment service and operation. 6. Include setting drawings, templates, and instructions for installing anchor bolts and other anchorages. 7. Include diagrams for power, signal, and control wiring.
777 | 118226 | FACILITY WASTE COMPACTORS | 1.5-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
778 | 118226 | FACILITY WASTE COMPACTORS | 1.5-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of waste compactor.
779 | 118226 | FACILITY WASTE COMPACTORS | 1.5-C | INFORMATIONAL SUBMITTALS | Reports | Field quality-control reports.
780 | 118226 | FACILITY WASTE COMPACTORS | 1.6-A | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For waste compactors to include in operation and maintenance manuals.
781 | 118226 | FACILITY WASTE COMPACTORS | 1.6-B | CLOSEOUT SUBMITTALS | Maintenance Service | Continuing Maintenance Proposal : From Installer to Owner, in the form ofa standard five-year maintenance agreement, starting on date maintenance service is concluded. State services, obligations, conditions, and terms for agreement period and for future renewal options.
786 | 118226 | FACILITY WASTE COMPACTORS | 3.4-A | MAINTENANCE SERVICE | Maintenance Data | Maintenance Service : Beginning at Substantial Completion, initial maintenance service shall include 12 months' full maintenance by skilled employees of waste-compactor Installer. Include monthly preventive maintenance, repair, or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper waste-compactor operation. Parts and supplies shall be manufacturer's authorized replacement parts and supplies.
787 | 118226 | FACILITY WASTE COMPACTORS | 3.5-A | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain waste compactors according to manufacturer's written instructions and ANSI Z245.2.
788 | 122413 | ROLLER WINDOW SHADES | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include construction details, material descriptions, dimensions of individual components and profiles, features, finishes, and operating instructions for roller shades.
789 | 122413 | ROLLER WINDOW SHADES | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : Show fabrication and installation details for roller shades, including shadeband materials, their orientation to rollers, and their seam and batten locations. 1. Motor-Operated Shades: Include details of installation and diagrams for power, signal, and control wiring.
790 | 122413 | ROLLER WINDOW SHADES | 1.3-C | ACTION SUBMITTALS | Samples | Samples : For each exposed product and for each color and texture specified, 10 inches long.
791 | 122413 | ROLLER WINDOW SHADES | 1.3-D | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of roller shade. 1. Shadeband Material: Not less than 3 inches square. Mark interior face of material if applicable. 2. Roller Shade: Full-size operating unit, not less than 16 inches wide by 36 inches long for each type of roller shade indicated. 3. Installation Accessories: Full-size unit, not less than 10 inches long.
792 | 122413 | ROLLER WINDOW SHADES | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
793 | 122413 | ROLLER WINDOW SHADES | 1.4-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For each type of shadeband material.
794 | 122413 | ROLLER WINDOW SHADES | 1.4-C | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : For each type of shadeband material, for tests performed bya qualified testing agency.
795 | 122413 | ROLLER WINDOW SHADES | 1.5-A | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For roller shades to include in maintenance manuals.
796 | 122413 | ROLLER WINDOW SHADES | 1.6-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Roller Shades: Full-size units equal to 5 percent of quantity installed for each size, color, and shadeband material indicated, but no fewer than two units.
798 | 122413 | ROLLER WINDOW SHADES | 1.7-B | QUALITY ASSURANCE | Mockups | Mockups : Build mockups to verify selections made under Sample submittals, to demonstrate aesthetic effects, and to set quality standards for fabrication and installation. 1. Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing. 2. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
799 | 122413 | ROLLER WINDOW SHADES | 3.5-A | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain motor-operated roller shades.
800 | 123553.13 | METAL LABORATORY CASEWORK | 1.3-A | PREINSTALLATION MEETINGS | Meetings | Preinstallation Conference : Conduct conference at Project site.
801 | 123553.13 | METAL LABORATORY CASEWORK | 1.3-B | PREINSTALLATION MEETINGS | Meetings | Keying Conference : Conduct conference at Project site. Incorporate keying conference decisions into final keying requirements.
802 | 123553.13 | METAL LABORATORY CASEWORK | 1.5-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product.
803 | 123553.13 | METAL LABORATORY CASEWORK | 1.5-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For laboratory casework. 1. Include plans, elevations, sections, and attachments to other work including blocking and reinforcements required for installation. 2. Indicate types and sizes of casework. 3. Indicate manufacturer's catalog numbers for casework. 4. Show fabrication details, including types and locations of hardware. 5. Indicate locations and types of service fittings. 6. Include details of utility spaces showing supports for conduits and piping. 7. Include details of support framing system. 8. Include details of exposed conduits, if required, for service fittings. 9. Indicate locations of and clearances from adjacent walls, doors, windows, other building components, and laboratory equipment. 10. Include coordinated dimensions for laboratory equipment specified in other Sections.
804 | 123553.13 | METAL LABORATORY CASEWORK | 1.5-C | ACTION SUBMITTALS | Keying Schedule | Keying Schedule : Include schematic keying diagram, and index each key set to unique designations that are coordinated with the Contract Documents.
805 | 123553.13 | METAL LABORATORY CASEWORK | 1.5-D | ACTION SUBMITTALS | Samples | Samples : For casework finishes and materials requiring color selection.
806 | 123553.13 | METAL LABORATORY CASEWORK | 1.5-E | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For casework finishes and materials requiring color selection.
807 | 123553.13 | METAL LABORATORY CASEWORK | 1.5-F | ACTION SUBMITTALS | Samples | Samples for Verification : For each type of casework, exposed-hardware, and countertop- material finish, in manufacturer's standard sizes. 1. Full-Size Samples: Maintain at Project site during construction in an undisturbed condition asa standard for judging the completed Work. Unless otherwise indicated, approved sample units may become part of the completed Work if in undisturbed condition at time of Substantial Completion. Notify Architect of their locations.
808 | 123553.13 | METAL LABORATORY CASEWORK | 1.5-G | ACTION SUBMITTALS | Delegated-Design Submittal | Delegated-Design Submittal : For laboratory casework indicated to comply with seismic performance requirements, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.
809 | 123553.13 | METAL LABORATORY CASEWORK | 1.6-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For manufacturer.
810 | 123553.13 | METAL LABORATORY CASEWORK | 1.6-B | INFORMATIONAL SUBMITTALS | Test Reports | Product Test Reports : - 1. Casework: Based on evaluation of comprehensive tests performed bya qualified testing agency, indicating compliance of laboratory casework with requirements of specified product standard and system structural performance specified in "Performance Requirements" Article. 2. Countertop Surface Material: Based on evaluation of comprehensive tests performed bya qualified testing agency, indicating compliance of laboratory countertop surface material with requirements specified for chemical and physical resistance.
811 | 123553.13 | METAL LABORATORY CASEWORK | 1.7-A | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish complete touchup kit for each type and color of casework finish provided. Include fillers, primers, paints, and other materials necessary to perform permanent repairs to damaged laboratory casework finish.
812 | 123553.13 | METAL LABORATORY CASEWORK | 1.7-B | MAINTENANCE MATERIAL SUBMITTALS | Attic Stock | Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. 1. Cabinet Mounting Clips and Related Hardware: Quantity equal to 5 percent of amount installed, but no fewer than 20 each type. 2. Modular Countertop Units: Two extra units of each length and material installed.
814 | 123553.13 | METAL LABORATORY CASEWORK | 3.8-A | SERVICE-FITTING SCHEDULE | Schedules | Water Service Fitting, Type WF-1 : - 1. Fitting Type: Swing-spout mixing faucet. 2. Outlet: Vacuum breaker and removable serrated outlet. 3. Mounting: Deck mounted. 4. Additional Requirements: Self-closing valves 5. Refer to fixture schedule: P5-65-70001 Laboratory Gas Service Fitting, Type GF-1 : - 1. Service: Air. 2. Fitting Type: Turret 3. Outlets: Three 4. Outlet Type: Straight. 5. Valve Type: Ground-key cock. 6. Refer to fixture schedule: P5-65-70001 Electrical Service Fitting, Type EF-1 : - 1. Fitting Type: Recessed or Line mounted 2. Device: Two duplex receptacles 3. Additional Requirements: GFCI receptacles. Communication Service Fitting, Type CF-1 : - 1. Fitting Type: Line mounted. 2. Device: Two duplex receptacles. Electrical and Communication Service Fitting, Type ECF-1 : - 1. Fitting Type: Recessed or Line mounted. 2. Device: duplex receptacles and two duplex communication receptacles. 3. Additional Requirements: GFCI receptacles.
815 | 123623.13 | PLASTIC-LAMINATE-CLAD COUNTERTOPS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. 1. Include data for fire-retardant treatment from chemical-treatment manufacturer and certification by treating plant that treated materials comply with requirements.
816 | 123623.13 | PLASTIC-LAMINATE-CLAD COUNTERTOPS | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For plastic-laminate-clad countertops. 1. Include plans, sections, details, and attachments to other work. Detail fabrication and installation, including field joints. 2. Show locations and sizes of cutouts and holes for items installed in plastic-laminate-clad countertops. 3. Apply AWI Quality Certification Program label to Shop Drawings.
817 | 123623.13 | PLASTIC-LAMINATE-CLAD COUNTERTOPS | 1.3-C | ACTION SUBMITTALS | Samples | Samples : Plastic laminates in each type, color, pattern, and surface finish required in manufacturer's standard size.
818 | 123623.13 | PLASTIC-LAMINATE-CLAD COUNTERTOPS | 1.3-D | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For plastic laminates.
819 | 123623.13 | PLASTIC-LAMINATE-CLAD COUNTERTOPS | 1.3-E | ACTION SUBMITTALS | Samples | Samples for Verification : As follows: 1. Plastic Laminates: For each type, color, pattern, and surface finish required, 12 by 12 inches in size. 2. Fabrication Sample: For each type and profile of countertop required, provide one sample applied to core material with specified edge material applied to one edge.
820 | 123623.13 | PLASTIC-LAMINATE-CLAD COUNTERTOPS | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
821 | 123623.13 | PLASTIC-LAMINATE-CLAD COUNTERTOPS | 1.4-B | INFORMATIONAL SUBMITTALS | Certificates | Product Certificates : For the following: 1. Composite wood and agrifiber products. 2. High-pressure decorative laminate. 3. Chemical-resistant, high-pressure decorative laminate. 4. Adhesives.
822 | 123623.13 | PLASTIC-LAMINATE-CLAD COUNTERTOPS | 1.4-C | INFORMATIONAL SUBMITTALS | Certificates | Quality Standard Compliance Certificates : AWI Quality Certification Program.
823 | 123623.13 | PLASTIC-LAMINATE-CLAD COUNTERTOPS | 1.4-D | INFORMATIONAL SUBMITTALS | Reports | Evaluation Reports : For fire-retardant-treated materials, from ICC-ES.
826 | 123661.16 | SOLID SURFACING COUNTERTOPS | 1.3-A | ACTION SUBMITTALS | Product Data | Product Data : For countertop materials and sinks.
827 | 123661.16 | SOLID SURFACING COUNTERTOPS | 1.3-B | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : For countertops. Show materials, finishes, edge and backsplash profiles, methods of joining, and cutouts for plumbing fixtures. 1. Show locations and details of joints. 2. Show direction of directional pattern, if any.
828 | 123661.16 | SOLID SURFACING COUNTERTOPS | 1.3-C | ACTION SUBMITTALS | Samples | Samples for Initial Selection : For each type of material exposed to view.
829 | 123661.16 | SOLID SURFACING COUNTERTOPS | 1.3-D | ACTION SUBMITTALS | Samples | Samples for Verification : For the following products: 1. Countertop material, 6 inches square. 2. Wood trim, 8 inches long. 3. One full-size solid surface material countertop, with front edge and backsplash, 8 by 10 inches, of construction and in configuration specified.
830 | 123661.16 | SOLID SURFACING COUNTERTOPS | 1.4-A | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For fabricator.
831 | 123661.16 | SOLID SURFACING COUNTERTOPS | 1.5-A | CLOSEOUT SUBMITTALS | Maintenance Data | Maintenance Data : For solid surface material countertops to include in maintenance manuals. Include Product Data for care products used or recommended by Installer and names, addresses, and telephone numbers of local sources for products.
834 | 123661.16 | SOLID SURFACING COUNTERTOPS | 1.6-C | QUALITY ASSURANCE | Mockups | Mockups : Build mockups to demonstrate aesthetic effects and to set quality standards for fabrication and execution. 1. Build mockup of typical countertop as shown on Drawings. 2. Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.
835 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.10 | WARRANTY..................................................................................................................................... 3 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 4
846 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.10.-1 | WARRANTY | Manufacturers Warranty | Manufacturer's Special Warranty : Manufacturer agrees to repair, restore, or replace elevator work that fails in materials or workmanship within specified warranty period. a. Failures include, but are not limited to, operation or control system failure, including excessive malfunctions; performances below specified ratings; excessive wear; unusual deterioration or aging of materials or finishes; unsafe conditions; need for excessive maintenance; abnormal noise or vibration; and similar unusual, unexpected, and unsatisfactory conditions. b. Warranty Period: 1 year from date of Substantial Completion of the project.
836 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.4.-1 | ACTION SUBMITTALS | Product Data | Product Data : For each type of product. a. Include capacities, sizes, performances, operations, safety features, finishes, and similar information. b. Include Product Data for car enclosures, hoistway entrances, and operation, control, and signal systems.
837 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.4.-2 | ACTION SUBMITTALS | Shop Drawings | Shop Drawings : - a. Include plans, elevations, sections, and large-scale details indicating service at each landing, coordination with building structure, relationships with other construction, required hoistway dimensions and clearances and locations of equipment. b. Include large-scale layout of car-control station and standby power operation control panel. c. Indicate maximum dynamic and static loads imposed on building structure at points of support, and maximum and average power demands.
838 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.4.-3 | ACTION SUBMITTALS | Samples | Samples for Verification : For exposed car, hoistway door and frame, and signal equipment finishes; 3- inch-square Samples of sheet materials; and 4-inch lengths of running trim members.
839 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.5.-1 | INFORMATIONAL SUBMITTALS | Qualification Data | Qualification Data : For Installer.
840 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.5.-2 | INFORMATIONAL SUBMITTALS | Certificates | Manufacturer Certificates : Signed by elevator manufacturer certifying that hoistway and pit layout and dimensions, as indicated on Drawings, and electrical service including standby power generator, as shown and specified, are adequate for elevator system being provided.
841 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.5.-3 | INFORMATIONAL SUBMITTALS | Sample Warranty | Sample Warranty : For special warranty.
842 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.6.-1 | CLOSEOUT SUBMITTALS | O&M Manuals | Operation and Maintenance Data : For elevators to include in emergency, operation, and maintenance manuals. a. Submit manufacturer's or Installer's standard operation and maintenance manual, according to ASME A17.1/CSA B44.
843 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.6.-2 | CLOSEOUT SUBMITTALS | Certificates | Inspection and Acceptance Certificates and Operating Permits : As required by authorities having jurisdiction for normal, unrestricted elevator use.
844 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 1.6.-3 | CLOSEOUT SUBMITTALS | Maintenance Service | Continuing Maintenance Proposal : Submita continuing maintenance proposal from Installer to Owner, in the form ofa standard two-year maintenance agreement, starting on date initial maintenance service is concluded. State services, obligations, conditions, and terms for agreement period and for future renewal options.
850 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 3.5.-1 | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to operate, adjust, and maintain elevators. Check operation of each elevator with Owner's personnel present before date of Substantial Completion and again not more than one month before end of warranty period. Determine that operation systems and devices are functioning properly.
851 | 142123.16 | MACHINE ROOM-LESS ELECTRIC TRACTION PASSENGER E | 3.6.-1 | MAINTENANCE SERVICE | Maintenance Data | Initial Maintenance Service : Beginning at Substantial Completion, maintenance service shall include 12 months' full maintenance by skilled employees of elevator Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper elevator operation at rated speed and capacity. Parts and supplies shall be manufacturer's authorized replacement parts and supplies. a. Perform maintenance during normal working hours. b. Perform emergency callback service during normal working hours with response time of two hours or less. c. Include 24-hour-per-day, 7-day-per-week emergency callback service with response time of two hours or less.
853 | 184043 | ENTER THE SPEC SECTION NAME | 1.3 | BID REQUIREMENTS | Product Data | The bid data shall provide all technical information relevant to the product being provided, including but not limited to, all the information shown in the attached schedule(s). It is the responsibility of the supplier to highlight any variances the equipment has with the requirements of this specification. Information shall be provided in the same measurement units as indicated in the schedule(s). Product data shall also be included at time of bid, including dimensions, weights, capacities, component performance, electrical characteristics, casing construction details, section splits, gauges and material finishes. The bids shall provide independent fan curves for operating/design conditions [not fan tables], with specified operating/design points clearly plotted (include internal pressure drop calculation). The bids shall provide coil selection worksheets, clearly showing proper consideration for altitude, air density, glycol corrections and indicate coil tube fin and casing construction. The manufacturer shall submit preliminary manufacturers recommended installation instructions with bid. The manufacturer shall havea list of all exceptions to the specification at time of bid.
854 | 184043 | ENTER THE SPEC SECTION NAME | 1.4 | SUBMITTALS | General | Product data shall include dimensions, weights, capacities, certifications, component performance, electrical characteristics, casing construction details, wiring interconnections, gauges and material finishes. The submittal shall provide all technical information relevant to the product being provided, including but not limited to, all the information shown in the attached schedules and drawings(s). It is the responsibility of the supplier to highlight any variances the equipment has with the requirements of this specification whether or not pre-approval has been obtained. Information shall be provided in the same measurement units as indicated in the schedules and drawings(s). The submittal(s) shall provide independent fan curves for operating/design conditions [not fan tables], with specified operating/design points clearly plotted. The submittal(s) shall provide coil selection worksheets, clearly showing proper consideration for altitude, air density, glycol corrections and indicate coil tube fin and casing construction. The submittal(s) shall provide filter information, including: initial (clean) APD, final (dirty) APD, dust spot efficiency, final dust holding capacity, filter media description, filter frame details, and filter removal details. The manufacturer shall submit sound power levels for both air handling unit inlet, outlet and radiated at rated capacity. The manufacturer shall submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring. The manufacturer shall submit the manufacturers recommended installation instructions. The submittal shall include calculation of required trap depth at drain pan connection(s) with internal static pressures at design operating conditions
855 | 184043 | ENTER THE SPEC SECTION NAME | 1.5 | OPERATION AND MAINTENANCE DATA | O&M Manuals | The manufacturer shall submit operation and maintenance data under provisions of Section 230855. The manufacturer shall include instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists, and wiring diagrams.
856 | 184043 | ENTER THE SPEC SECTION NAME | 1.6 | WARRANTY | Warranty | A warranty shall be provided by the manufacturer for the air handling unit(s). Sub-Contractor shall assume manufacturers warranty in its entirety, as if the equipment had been purchased by the Sub-Contractor. It shall be the responsibility of the Sub-Contractor, during the term of the warranty, to respond to reports of evident malfunction or failure, as though the equipment had been furnished by him, conduct the necessary diagnostic efforts, and if the malfunction is deemed by him to be the manufacturers warranty liability, to so resolve this responsibility with the manufacturer as the Owners agent.
858 | 184043 | ENTER THE SPEC SECTION NAME | 3.7 | EXTRA FILTER STOCK | Attic Stock | The manufacturer will provide one extra set of pre-filters for each air handling unit. Install new filters at completion of air handling system work, and prior to testing, adjusting, and balancing work. Obtain receipt from testing and balancing Sub-Contractor that new filters have been installed.
859 | 184043 | ENTER THE SPEC SECTION NAME | 3.8 | TRAINING | O&M Training And Demonstration | After successful start-up, furnish on-site instruction and training as follows: Furnish qualified personnel to instruct and train the Catalent personnel.
861 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.14 | SUBMITTALS - WITH BID | General | The following is the minimum information required to be submitted with the bid. The Construction Manager may require additional information. Client References: Submit three (3) client references from Life Science laboratories or manufacturers that have BMS Installations provided by this BMS Vendor. Statement of Compliance: The BMS Vendor shall guarantee that all services included in the scope of supply, are in strict accordance with the requirements of the Bid Documents. The BMS Vendor shall return with his quotation a statement of compliance. This shall clearly and explicitly detail any variances from the Bid Documents, however minor, referenced against the specific section of the document or drawing. It shall be assumed that the BMS Vendor is fully compliant with all documents not listed in this statement. Sample Graphic Screens: Submit representative sample graphic screens in color that are typical of what will be provided for this type of project. Sample Sequence of Operation: Submita representative sample sequence of operation that is typical of what will be provided for this type of project. System Architecture Drawing: Submit drawing indicating overall network of Controllers, PCs, Printers and all major system components indicating how they are networked, how many Controllers are being provided and what they Control. Application Software//Development: Provide documented procedures for controller and workstation software development. Procedures shall address developer training, pre-development documents, development techniques, and change control asa minimum. Preliminary Schedule: Providea preliminary project schedule indicating proposed work phases and sequences. Include in schedule asa minimum, submittals, equipment release, delivery, fabrication, equipment setting, construction activities, and start-up. Project Documentation: Where bid documents call for the production and supply ofa range of drawings, the BMS Vendor shall describe in detail how these drawings will be produced and issued in coordination with the proposed construction program and with Owner review and approval procedure. All project drawings shall be numbered in accordance with the BMS Vendors standard drawing numbering system. A detailed drawing schedule shall be supplied to the Owner within two weeks of contract award. This shall be updated every two weeks until all drawings have been finally approved. Quality and Project Plan (QPP): Submit preliminary QPP or sample ofa comparable QPP, as defined in Section 1.7.1.
862 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.15 | SUBMITTALS - AFTER AWARD OF CONTRACT | General | Preparation All project submittals shall be in electronic Portable Document Format (.pdf) readable by Adobe, Bluebeam, or comparable program. All submittals shall be posted to the project website, in the folder designated. Details on project submittal procedures, the project website and uploading to it will be given during the kick-off meeting after award by the Construction Manager. Submittals shall be printed to.pdf, not printed as hardcopy and scanned to.pdf. Annotations to.pdf to clarify information, such as indicating specific options on an instrument cutsheet, should be done using editing tools in Adobe, Bluebeam, or comparable program, not hand-marked and scanned. The Engineer or Owner reserves the right to reject submittals without review if the.pdf is not readable or if pixilation occurs on zooming in, rendering enlarged content unreadable. Schedules Providea project schedule indicating proposed work phases and sequences. Include in schedule asa minimum, approvals, equipment release, delivery, fabrication, equipment setting, startup, punch listing, and cleanup. Prepare and submita complete schedule of submittals. Coordinate the submittal schedule with the BMS Vendors construction schedule. Prepare the submittal schedule in chronological order. The submittal schedule shall be updated every two weeks and re-issued to the Owner until all submittals have been finally approved. Coordination Coordinate preparation and processing of submittals with performance of construction activities. Transmit each submittal sufficiently in advance of performance of related construction activities to avoid schedule delays. Coordinate each submittal with fabrication, purchasing, testing, delivery, other submittals, and related activities that requires sequential activity. Coordinate transmittal of different types of submittals for related elements of the work so processing will not be delayed by the need to review submittals concurrently for coordination. The Engineer or Owner reserves the right to withhold action ona submittal requiring coordination with other submittals until related submittals are received. Processing Allow sufficient review time so that installation will not be delayed asa result of the time required to process submittals, including time to resubmit and including time to coordinate with other submittals. If an intermediate submittal is necessary, process the same as the initial submittal. Submittals Documents for Review The following is the minimum required documents that are required as submittals. Component Data: includes catalog cuts, sketches, or bulletins indicating performance characteristics, features of equipment, controls, instrumentation, equipment dimensions, materials of construction, estimated weights, heat rejection load when operating, auxiliaries, specialties, or accessories furnished, roughing-in or anchor diagrams and templates, manufacturer's installation instructions, service clearance requirements, standard color charts, and wiring diagrams. Where Component Data includes information on several products, some of which are not required, annotate product data to indicate specific product and options being provided. For instrumentation, includea list of applicable tag numbers in accordance with the project P&IDs and instrument list. The Engineer or Owner reserves the right to rejecta submittal if the provided data is generic. Provide complete instrument schedule indicating instrument tag number, instrument type, manufacturer model number, size for all instruments in the BMS Vendors scope to provide. Provide complete control valve schedule indicating tag number, valve type, manufacturer, model number, size, Cv and maximum shutoff pressure for each control valve on the project. Provide calculations for all components within the BMS Vendors scope that require sizing (such as control valves, damper actuators). Shop Drawings: Submit shop drawings for control system containing the following information. Any product or work indicated on drawings that is not provided by the BMS Vendor shall be clearly identified. System Architecture Drawing indicating overall network of Controllers, Remote I/O panels, Application Specific Controllers, PCs, Printers and all major system components indicating how they are networked, how many Controllers are being provided and what they control. Include BOM for all components. Include addressing details for each component (IP address, MAC address, node, instance, etc. as applicable). BMS Network plan showing the location of BMS Network drops and type of drop (ceiling, wall, etc.). This shall include mark-ups to the Engineers automation network plan drawings showing any revision to the location of drops identified. Schematic flow diagram of system indicating fans, pumps, coils, dampers, valves, and control devices as applicable to project. I/O List, which shall include point names and addresses for each control device labeled with setting or adjustable range of control. Interlock, Alarm, and Permissive list, including setpoints and criticality level. Interlock, Alarm, and Permissive list may be included in points list, sequence of operations, ora separate document. The list must address both hardware and software interlocks, alarms, and permissives. Schematic Drawings shall include elevation and plan views, and indicate all connections, attachments, and details to indicate field required general details of assembly, etc. Wiring Diagrams shall detail wiring for signal, control, and power, differentiating between manufacturer-installed wiring and field-installed wiring. Wiring diagrams to include annotation for wire and cable labels and include terminal identification. Details of control panels, including panel layout, controls, instruments, labeling, and bill of materials. Mark-ups to the Engineers General Arrangement drawings showing any revision to the location of BMS panels. Detailed sequence of operations based on the detailed sequences of control provided by the Engineer. Application Software/Documentation: Provide documented procedures for controller and OIT software development. Procedures shall address developer training, pre-development documents, development techniques, and change control asa minimum. The controller and OIT programming shall be done in English, ina well-organized fashion that shall provide complete listings and descriptions of data files, program files, and program annotation to adequately describe software functionality. Additional written documentation explaining program structure, modules, data file layout, sequences, and password-controlled parameters shall be supplied. The controller program shall include descriptive annotation, hardwired I/O listings with descriptive labels, and listings with descriptive labels of any internal flags, timers, counters, memory registers, PID functions, and any other special functions used in the control program application. After the system installation and operational startups are complete, resubmit the updated versions complete with documentation on each change that was made to the previously released submittals shall be made. This documentation shall be delivered to the Owner and Owners representative five (5) weeks prior to delivery of the equipment to the Owner. This will allow two weeks for the Owner and Owner's representative to review. The Owner's representative may, at the end of the review, issue to the BMS Vendora list of needed clarifications or changes to the software. Following the review, the BMS Vendor shall implement any changes directed by the Owner within the remaining time period prior to delivery. Graphical User Interface Screens: Submit copies of proposed graphic screens in color with written notation indicating how the screen will operate dynamically. Software Code Listing: Provide an electronic copy of canned configurable and custom application software for Owner review at essential milestones throughout the life of the project, includinga final turnover of as As-Built. Protocol Implementation Conformance Statement (PICS): A BACnet PICS shall be submitted for each BACnet controller and device in the system. This applies to native BACnet systems only. Quality and Project Plan (QPP): As defined in Section 1.7.1. Testing Procedures: Submit detailed Factory Acceptance Test (FAT) procedure for review and approval, for both hardware (controller panels) and software. Test shall fully exercise all functionality of the Building Management System, simulated as closely as possible to field installed conditions. Submit detailed Site Acceptance Test (SAT) procedure for review and approval. Test shall fully exercise all functionality of the Building Management System, making use of installed control system hardware. Testing procedures shall include full loop checks and calibrations of all instrumentation, from instrument to graphic screen, not just continuity checks. Testing shall be performed and documented to verify that the system operates as specified in the sequence of operations. Completed test documentation shall be supplied to demonstrate that the installed system performs as specified. Final test documentation shall include signed Factory Acceptance Testing and Site Acceptance Testing procedures. Submittals for Record All documents detailed in Section 1.15.5 shall be submitted for record inclusive of all Owner and Engineer comments and any approved changes since the approval of the review submittal. In addition, the following data shall be submitted: Product Data: Product data is deemed to mean supplemental information such as certificates of conformance, material certification, certification of special cleaning, factory calibration certificates. These kinds of documents are not req
863 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.17 | WARRANTY | Warranty | The BMS Vendor shall providea comprehensive warranty which shall cover both parts and labor and be not less than one year from signing of the final acceptance certificate. Any manufacturing defects arising during the warranty period shall be corrected without additional cost to the Owner. The BMS Vendor shall provide full details of warranty terms and conditions. The BMS Vendor shall include costs fora preventative maintenance agreement asa separate line item within their bid. The preventative maintenance agreement shall includea minimum of quarterly service visits, include defective parts replacement and commence upon completion of the BMS system installation and acceptance by the Owner.
864 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.18 | SPARE PARTS AND SPARE PARTS MAINTENANCE | Attic Stock | The BMS Vendor shall providea list of recommended spare parts with their bid, including costs. In addition, the BMS Vendor shall provide, asa separate line item, information and costs to provide Spare Parts Management, if sucha program isa standard offering.
865 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.19-1 | TRAINING | O&M Training And Demonstration | Explanation of drawings, operations, and maintenance manuals.
866 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.19-2 | TRAINING | O&M Training And Demonstration | Walk-through of the job to locate control components.
867 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.19-3 | TRAINING | O&M Training And Demonstration | Operator workstation and peripherals.
868 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.19-4 | TRAINING | O&M Training And Demonstration | DDC controller and ASC operation/function.
869 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.19-5 | TRAINING | O&M Training And Demonstration | Operator control functions including graphic generation and field panel programming.
870 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.19-6 | TRAINING | O&M Training And Demonstration | Operation of portable operator's terminal.
871 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.19-7 | TRAINING | O&M Training And Demonstration | Explanation of adjustment, calibration, and replacement procedures.
872 | 184043 _revised_1135 | ENTER THE SPEC SECTION NAME | 1.19-8 | TRAINING | O&M Training And Demonstration | Student binder with training modules. Providea minimum of four on-site or classroom training sessions, three days each, throughout the contract period for personnel designated by the owner. Provide two additional training sessions at 6 and 12 months following buildings turnover. Each session shall be three days in length and must be coordinated with the building owner. Train the designated staff of the Owner to enable them to do the following: Day-to-day Operators: Proficiently operate the system Understand control system architecture and configuration Understand BMS system components Understand system operation, including system control and optimizing routines (algorithms) Operate the workstation and peripherals Log on and off the system Access graphics, point reports, and logs Adjust and change system set points, time schedules, and holiday schedules Recognize malfunctions of the system by observation of the printed copy and graphical visual signals Understand system drawings and Operation and Maintenance manual Understand the job layout and location of control components Access data from controllers and ASCs Operate portable operators terminals Advanced Operators: Make and change graphics on the workstation Create, delete, and modify alarms, including annunciation and routing of these Create, delete, and modify point trend logs and graph or print these both on an ad-hoc basis and at user- definable time intervals Create, delete, and modify reports Add, remove, and modify systems physical points Create, modify, and delete programming Add panels when required Add operator interface stations Create, delete, and modify system displays, both graphical and others Perform system field checkout procedures Perform controller unit operation and maintenance procedures Perform workstation and peripheral operation and maintenance procedures Perform system diagnostic procedures Configure hardware including PC boards, switches, communication, and I/O points Maintain, calibrate, troubleshoot, diagnose, and repair hardware Adjust, calibrate, and replace system components System Managers/Administrators: Maintain software and prepare backups Interface with job-specific, third-party operator software Add new users and understand password security procedures These courses and objectives will be divided into three logical groupings. Participants may attend one or more of courses, depending on level of knowledge required. Classroom training shall be done usinga network of working controllers representative of the installed hardware.
874 | 184043 _revised_1628 | ENTER THE SPEC SECTION NAME | 1.9 | SUBMITTALS | General | The Vendor shall submita written control panel test procedure to the Owner for review and approval prior to executing the tests. The procedures shall detail installation inspection procedures, operation inspection procedures, and execution of these procedures. The Owner reserves the right to reproduce any drawing or print received from the Vendor, as may be required during the design and construction of this project and the preparation of the plant manual, despite any notice prohibiting the same appearing on the drawing or print. After the order is placed, the Vendor shall submit all data and drawings listed in the governing scope specification as issued with the Request for Quotation. The Owner job order number, purchase order number, project name, control panel name, and control panel identification number shall be shown on each drawing. The drawings submitted shall show the following asa minimum: General Arrangement drawings of the external and internal layouts, with Bill of Materials detailing responsibility of supply. Cross sections and details, as required, to satisfy the Owner that all components are in conformance with the intent of the specification, and are satisfactory from the standpoint of design and physical arrangement. Internal control panel wiring diagrams showing terminal numbers, wire and cable labels, wire colors and gauge, and component labels. Pneumatic tubing layout, showing tubing labels and component labels. All information required by the Owner for design and location of all connecting furnished structural, mechanical, or electrical items such as foundations, steel supports, piping, ducts, cables, conduit, and so forth. Dimensions and weight of the equipment. 120VAC power requirements, including FLA. After review by the Owner, a copy marked APPROVED, or REJECTED, REVISE AND RESUBMIT will be returned to the Vendor. If marked APPROVED, the Vendor may be directed to incorporate any changes per document mark-ups and/or attachments and resubmit to for record. If marked REVISE AND RESUBMIT, the required changes shall be incorporated by the Vendor and clearly identified, and the drawings shall again be submitted to the Owner for approval. If the Vendor elects not to incorporate the revisions, the Vendor shall inform the Owner that the suggested revisions cannot be made without prejudice to the Vendors responsibility under warranty. Arrangements for production scheduling shall not be deferred pending approval of drawings.
878 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-1 | SUBMITTALS | Product Data | Product Data : Manufacturer's catalog cut sheets and other published technical data for each of the following: a. Nameplates, instructions plates, signs and labels. b. Fasteners.
879 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-2 | SUBMITTALS | Samples | Samples : Provide samples of each color, lettering style, and other graphic representation required for identification materials. Provide samples of labels and signs. No material is to be ordered without this approval.
880 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-3 | SUBMITTALS | Schedules | Providea listing of proposed names, abbreviations and other designations used in identification. Provide an electronic copy of the schedule of proposed tags, nameplates and engraving for Owner approval. No material is to be ordered without this approval.
881 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-4 | SUBMITTALS | General | Providea final and complete, electronic listing of all applied tags, nameplates and engravings.
882 | 200553 | TAGGING AND IDENTIFICATION | 1.4.-5 | SUBMITTALS | Maintenance Data | Providea Hand Valve schedule as an electronic version in Microsoft Excel. Mark valves which are intended for emergency shut-off and similar special uses, by special flags, in margin of schedule. Furnish additional copies of schedule for Maintenance Manuals. Valve Schedule shall include the following information: a. Piping system b. System abbreviation (CW, CHWS, DI, WFI, CS60, CAP25, etc.) c. Valve identification number d. Location of valve (room or space) e. Type of valve (gate, ball, automatic control, etc.) f. Manufacturer and manufacturer's catalog number g. Indicate valves intended for emergency shutoff or other special use
885 | 220411 | WATER DISTRIBUTION SPECIALTIES | 1.2 | SUBMITTALS | General | Product data for each item specified herein.
890 | 220440 | PLUMBING FIXTURES | 1.2 | EXTRA STOCK................................................................................................................................. 1 | Attic Stock | PART 2. - PRODUCTS.......................................................................................................................................... 1
892 | 220440 | PLUMBING FIXTURES | 1.2 | EXTRA STOCK | Attic Stock | Furnish one (1) each of any special wrenches and other devices necessary for servicing plumbing fixtures and trim to Owner. Furnish faucet repair kits complete with all necessary washers, springs, pins, retainers, packings, O-rings, sleeves, and seats ina quantity of one kit for each 40 faucets.
894 | 220458 | FUEL FIRED DOMESTIC WATER HEATERS | 1.1 | SUBMITTALS | General | Submittals shall comply with the requirements of Section 230010, Basic Mechanical Requirements. In addition, provide the following: Certificates: Certificates of Shop Inspection and Data Report as required by ASME Boiler and Pressure Vessel Code.
896 | 220458 | FUEL FIRED DOMESTIC WATER HEATERS | 3.3 | CLOSEOUT PROCEDURES | General | Training: Provide services of manufacturer's technical representative for four (4) hours minimum to instruct Owner's personnel in operation and maintenance of water heaters. Schedule training with Owner, provide at least seven (7) days notice to Owner, Contractor, and Engineer of training date.
899 | 220481 | COMPRESSED AIR EQUIPMENT | 1.3 | SUBMITTALS | General | Data Sheets The Vendor/Manufacturer shall complete all fields indicated as VS* (Vendor Specified) on each attached data sheet, as well as correct/modify any other fields and values as required and submit them as part of the final submittal documentation.
897 | 220481 | COMPRESSED AIR EQUIPMENT | 1.4 | WARRANTY..................................................................................................................................... 2 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 2
900 | 220481 | COMPRESSED AIR EQUIPMENT | 1.4 | WARRANTY | Warranty | Provide warranty in accordance with specification section 230010.
902 | 220481 | COMPRESSED AIR EQUIPMENT | 3.6 | DEMONSTRATION | O&M Training And Demonstration | The manufacturer will provide the services ofa factory authorized service representative to provide start-up service and to demonstrate and train the Owner's maintenance personnel as specified below. Coordinate with the manufacturer's representative. Training Train the Owner's maintenance personnel on start-up and shutdown procedures, troubleshooting procedures, and servicing and preventative maintenance schedules and procedures. Review with the Owner's personnel, the data contained in the Operating and Maintenance Manuals. Training with Owner should be scheduled at least seven (7) days in advance.
903 | 220488 | BULK LIQUID AND CYLINDER GAS STORAGE | 3.2 | MAINTENANCE | Maintenance Data | The Vendor shall fully schedule and document all maintenance work with the Owner prior to the commencement of any such work.
905 | 230010 | BASIC MECHANICAL REQUIREMENTS | 1.4 | WARRANTIES | Warranty | In addition to warranties called for in other sections of these specifications, work shall be warranted against defect due to faulty installation, manufacture, and component design. Warranties shall be fora period of not less than one (1) year, beginning on the later date of final acceptance by Owner, or equipment start-up. Upon written notice from the Owner or Engineer, promptly remedy, without cost to the Owner, any defects occurring or discovered during the warranty period.
906 | 230010 | BASIC MECHANICAL REQUIREMENTS | 1.5 | SUBMITTALS | General | General Provide submittals of material or equipment in accordance with the Submittal Requirement Schedule at the end of this specification section. Some sections have very specific submittal requirements, not indicated in this section, and therefore are indicated in that specific specification section. A submittal is required if an X is indicated for that column and item. Acceptable Manufacturers Subject to compliance with the requirements of the individual specification sections, provide materials and equipment from the indicated manufacturers only. Submittals of material or equipment manufactured by other than those indicated will be returned. If no manufacturers are indicated, then any product or material that complies with the specification and for the intended application is acceptable. If manufacturers are indicated, the first manufacturer in section list, or scheduled manufacturer or datasheet indicated manufacturer is the "basis of design", and all other indicated manufacturers are acceptable alternative manufacturers, as long as they also comply with the specification. It should be noted that there may be differences in dimension or installation requirements between the basis of design and others indicated and that additional work that may be required by other trades needs to be coordinated with the other trades and provided at no extra cost to the owner. Submittal Procedures Coordination: Coordinate preparation and processing of submittals with performance of construction activities. Transmit each submittal sufficiently in advance of performance of related construction activities to avoid delay. Coordinate each submittal with fabrication, purchasing, testing, delivery, other submittals and related activities that requires sequential activity. Coordinate transmittal of different types of submittals for related elements of the work so processing will not be delayed by the need to review submittals concurrently for coordination. The Owner or Owner's Representative reserves the right to withhold action ona submittal requiring coordination with other submittals until related submittals are received. Processing: Allow sufficient review time so that installation will not be delayed asa result of the time required to process submittals, including time for resubmittals. Allow ten working days for initial review. Allow additional time if processing must be delayed to permit coordination with subsequent submittals. The Owner or Owner's Representative will promptly advise the Contractor whena submittal being processed must be delayed for coordination. If an intermediate submittal is necessary, process the same as the initial submittal. Allow ten working days for reprocessing each submittal. No extension of contract time will be authorized because of failure to transmit submittals to the Owner or Owner's Representative sufficiently in advance of the work to permit processing. Submittal Preparation: Placea permanent label or title block on each submittal for identification. Indicate the name of the entity that prepared each submittal on the label or title block. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Contractor's review and approval markings and the action taken. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Owner's or Owner's Representative review and approval markings and the action taken. Include the following information on the label or title block for processing and recording action taken. Project name Date Name and address of Owner Name and address of Engineer Name and address of Contractor Name and address of subcontractor Name and address of supplier Name of manufacturer Number and title of appropriate Specification Section Drawing number and detail references, as appropriate Unique Submittal Number for each package Submittal Transmittal: Package each submittal appropriately for transmittal and handling. Transmittal shall list specification section for each item submitted. Transmit each submittal from Contractor to Owner or Owner's Representative usinga transmittal form. Submittals received from sources other than the Contractor will be returned without action. Submittals: Submit one (1) electronic copy of each required submittal ina single combined PDF format with all individual specification sections separated individually. The Engineer will mark and return one (1) electronic copy in PDF format with action taken and corrections or modifications required. Owner will retain one (1) electronic copy of returned document. Retain copy of each for O&M manuals or Enhanced Turn Over Packages (ETOPs). Schedules: Project schedules indicating proposed work phases and sequences. Include in schedule asa minimum, approvals, equipment release, delivery, fabrication, equipment setting, startup, punch, and cleanup. Submittal Schedule Prepare and submita complete schedule of submittals. Coordinate submittal schedule with the construction schedule. Prepare the schedule in chronological order. Provide the following information: Scheduled date for submittal Related Section number Submittal category Name of subcontractor Description of the part of the work covered Anticipated date for Engineer's final release or approval Schedule Updating: Revise the schedule after each meeting or activity, where revisions have been recognized or made. Issue the updated schedule to all parties involved. 1.5.1. Review Action The Contractor is responsible for all data and information on submittals, including quantities, sizes, dimensions, and compliance with the Drawings and Specifications. Checking by the Owner or Owner's Representative is only for general conformance with the design concept of the project and general compliance with the information given in the Contract Documents. Any action shown is subject to the requirements of the Drawings and Specifications. Contractor is responsible for dimensions and quantities, which shall be confirmed at the job site, and fabrication process and techniques of construction. On the submittal, record relevant information and requests for data. Record deviations from Contract Document requirements, including minor variations and limitations. Include Contractor's certification that information complies with Contract Document requirements. Except for submittals for record, information for similar purposes, where action and return is required or requested, the Owner will check each submittal, mark to indicate action taken, and return promptly. Compliance with specified characteristics is the Contractor's responsibility. 1.5.2. Shop Drawings Submit information, drawn to accurate scale. Highlight, encircle, or otherwise indicate deviations from the Contract Documents. Do not reproduce Contract Documents or copy standard information as the basis of Shop Drawings. Standard information prepared without specific reference to the Project is not considered Shop Drawings. Shop Drawings include fabrication and installation drawings, setting diagrams, schedules, patterns, templates and similar drawings, and directions for installation of anchorages. Include asa minimum the following information on drawings or diagrams: Dimensions Identification of products and materials included Compliance with specified standards Notation of coordination requirements Notation of dimensions established by field measurement Clearances for access and service Sheet Size: Except for templates, patterns and similar full-size drawings, submit Shop Drawings in PDF format at least 8" x 11", but no larger than 30" x 42". Initial Submittal: (Where Contractor desires product specific information or preliminary review prior to processing of final submittal.) Submit an electronic copy of prints in PDF format for the Owner's review. Final Submittal: Submit electronic copy of all prints. An electronic set of prints will be retained and maintained asa Record Document. The Owner's representative has the right to mark up the final submittal. Do not use Shop Drawings without an appropriate final stamp indicating action taken in connection with construction. 1.5.3. Coordination Drawings or 3D (BIM) Model: Mechanical, Electrical, Plumbing and Fire Protection Contract Drawings or 3D (BIM) model are diagrammatic. They are not intended to be precise; they are not intended to specify or to show every offset, fitting, and component. The purpose of the drawings or 3D (BIM) model is to indicatea systems concept, the main components of the systems, and the approximate geometrical relationships. Information and components shown on diagrams, but not shown on plans, and vice versa, shall apply or be provided as if expressly required on both. The contractor shall provide coordination drawings or 3D (BIM) model; detailing major elements, components, and systems of mechanical equipment and materials in relationship with other systems, installations, and building components. Indicate locations where space is limited for installation and access and where sequencing and coordination of installations are of importance to the efficient flow of the Work. Refer to the Project's BIM execution plan. Drawings or 3D (BIM) model shall include but shall not be limited to the following: Clearances for installing and maintaining installation. Clearances for servicing and maintaining equipment, including tube removal, filter removal, valves and space for equipment disassembly required for periodic maintenance. Equipment connections and support details. Exterior wall and roof penetrations. Fire-rated wall and floor penetrations. Sizes and locations of required concrete pads and bases. Valve stem movement. Plumbing systems, piping and equipment. HVAC
908 | 230038 | CONTROLLED ENVIRONMENTAL CHAMBER | 1.2 | SUBMITTALS | Product Data | Product Data: Submit manufacturer's technical data describing environmental chambers. The Data Sheet attached with this document shall be completed by all manufacturers submitting bids. This sheet shall be reviewed by the Owner/Designer and shall be used for final selection of manufacturer. All details must be provided as requested. All details denoted with VS (Vendor Supplied) must be provided as requested. Upon award, submit shop drawings showing layout, elevations, typical sections and details. Show plans, elevations and sections at not less than 1/4 inch scale; show details at not less than 1-1/2 inch scale. All utility requirements (power, water, drain, etc.) shall be provided. Wiring diagrams, piping schematics, component cut sheets and specifications shall also be provided after award and prior to startup. General: Show total layout of Controlled Environment Room(s) with relationship to adjacent building construction and equipment, fabrication and installation details, wall panel and roof panel data, door information, windows, materials, gages, fasteners, flashing, trim pieces and closures. Calculations: Supporting equipment selection. Indicate design loads added for door openings, air changes, direct supply air, lighting, personnel, process equipment, environmental room equipment and product load. Controls: Submit complete single-line diagrams, schematic diagrams, wiring diagrams, software descriptions, and all other details required to demonstrate that system has been coordinated and will properly function asa system. Provide outline dimensions, mounting details, weights, power requirements, console/cabinet/panel arrangements, system functional descriptions, Input/Output (I/O) point summary and I/O signal conditioning requirements. Refrigerants: Refrigerant Charge in pounds of refrigerant per ton of cooling capacity. Refrigerant Type. Equipment Type. Closeout Submittals: Operation and Maintenance Manuals: Include startup, operation and maintenance instructions, parts listing with sources indicated; recommended spare parts inventory listing, emergency instructions and similar information. Control systems: Include complete single-line diagrams, schematic diagrams, wiring diagrams, outline dimensions, mounting details, weights, power requirements, console/cabinet/panel arrangements, system functional descriptions, Input/Output (I/O) point summary and I/O signal conditioning requirements. Wiring diagrams to clearly show connetion points for remote monitoring signals. Testing Reports: Refrigerant Testing and Charging reports, Temperature Mapping, etc. Keys: Three (3) sets of marked and identified keys to operate all key operated functions, including control panel door
909 | 230038 | CONTROLLED ENVIRONMENTAL CHAMBER | 1.3 | WARRANTY | Warranty | Equipment, parts, and labor shall be guaranteed in written form fora period of one year from the date of chamber start-up and continuous normal operation. The warranty shall guarantee that the chamber shall maintain within the specified tolerance the selected temperature and humidity settings, shall be free from condensate on the outside of the chamber, and shall be free from defects due to faulty materials or workmanship. All refrigeration compressors included in any of the above equipment shall be provided with an additional four- year warranty on material (5 years total). All modular panels and door hardware shall be provided with an additional nine-year warranty on material (10 years total). All LED lamps shall be provided with an additional two-year warranty, minimum, on material (3 years total). The chamber installer shall providea service contract proposal and shall warrant the equipment fora period of one year. The service contract shall provide emergency callback service, free of charge, ona 24-hour, 7-daysa week basis during the warranty period. In addition, the manufacturer shall provide 8-hour emergency service and 24-hour non-emergency service by factory personnel or an authorized service center. The warranty shall not apply to equipment subjected to accidents, improper voltage, abuse, or misuse. The manufacturer shall prominently place the name of installer/service agency to be contacted during warranty period on the equipment. Services ofa factory-trained representative shall be made available for one (1) man-day minimum to provide instruction on the control system, review contents of the operation manual, and to provide general instruction on the proper use and care of the equipment. Multiple training sessions shall be made available within one (1) day. Instruction shall be provided by factory-trained technicians only. Sub-contractors shall not perform this service. In-Service Training Seminars: The manufacturer shall have available factory-instructed service seminars on this type of equipment to assure the maintenance staffs familiarity and competence with all operating and maintenance functions to allow self-directed maintenance if desired.
916 | 230135 | METERS AND GAUGES | 1.2 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS.......................................................................................................................................... 1
918 | 230135 | METERS AND GAUGES | 1.2 | SUBMITTALS | General | Provide submittal documents in compliance with requirements indicated in specification section 230010. Submittal must include tag number, range, process connection, materials of construction, and model number for all devices.
920 | 230135 _revised_790 | PRESSURE INDICATORS | 1.5 | SUBMITTALS | General | Provide submittal documents in compliance with requirements indicated in specification 230010. Provide drawings of each pipe hanger assembly and equipment support for each system application.
922 | 230241 | VIBRATION AND SEISMIC CONTROLS | 1.5 | SUBMITTALS | General | Product Data Include rated load, rated deflection, and overload capacity for each vibration isolation device. Illustrate and indicate style, material, strength, fastening provision, and finish for each type and size of seismic-restraint component used. Tabulate types and sizes of seismic restraints, complete with report numbers and rated strength in tension and shear as evaluated by an agency acceptable to authorities having jurisdiction. Annotate to indicate application of each product submitted and compliance with requirements. Coordination Drawings: Show coordination of seismic bracing or vibration pipe movement for piping and equipment with other systems and equipment in the vicinity, including other supports and seismic or vibration restraints. Welding certificates. Qualification Data: For professional engineer and testing agency.
940 | 230501 | MECHANICAL EQUIPMENT GENERAL REQUIREMENTS | 1.4 | SUBMITTALS................................................................................................................................... 3 | General | PART 2. - DESIGN REQUIREMENTS................................................................................................................ 6
942 | 230501 | MECHANICAL EQUIPMENT GENERAL REQUIREMENTS | 1.4 | SUBMITTALS | General | Provide submittals per the technical equipment specifications and commercial terms, in addition to the following requirements. 1.4.1. General All submittals shall display Owners Equipment tag number. Submittals shall be legible with sufficient space for comments. 1.4.2. Acceptable Manufacturers Provide materials and equipment only from the manufacturers indicated in the specification. Submittals of material or equipment manufactured by other than those indicated will be returned. If no manufacturers are indicated, then any product or material that complies with the specification for the intended application may be submitted for approval. 1.4.3. Submittal Procedures Coordination: A submittal schedule shall be prepared by the manufacturer and approved by the owner or the owners representative prior to award of P.O. Processing: Allow sufficient review time so that installation will not be delayed asa result of the time required to process submittals, including time for resubmittals. Allow ten working days for initial review. If an intermediate submittal is necessary, allow ten working days for reprocessing each submittal. No extension of contract time will be authorized because of failure to transmit submittals to the Owner or Owner's Representative sufficiently in advance of the work to permit processing. Submittal Preparation: Placea permanent label or title block on each submittal for identification. Indicate the name of the entity that prepared each submittal on the label or title block. Providea space approximately 4'' x 5'' on the label or beside the title block on Shop Drawings to record the Owner's or Owner's Representative review and approval markings and the action taken. Include the following information on the label or title block for processing and recording action taken. Project name Date Name and address of Owner Name and address of Engineer Name and address of Manufacturer Equipment number and equipment name Submittal Transmittal: Transmit each submittal from Manufacturers to Owner or Owner's Representative using a transmittal form. Submittals: Submit one (1) electronic copy of each required submittal ina single combined PDF format. The Engineer will mark and return one (1) electronic copy in PDF format with action taken and corrections or modifications required. The Owner will retain one (1) electronic copy of returned document. Retain copy of each final approved submittal for inclusion in O&M manuals. On the transmittal record relevant information and requests for data. On the form, or separate sheet, record deviations from Contract Document requirements, including minor variations and limitations. Electronic submittals from Contractor to Owner or Owners Representative are acceptable. The subject line shall clearly indicate the equipment/system being submitted including specification section number. The body of the email or fax cover sheet shall clearly list the information indicated in the Submittal Preparation section of this specification. Email attachments shall be in Microsoft Word, AutoCAD, MicroStation, PDF, TIFF or another approved format. 1.4.4. Submittals Definitions Manufacturers Qualifications: Provide standard literature, which illustrates the Manufacturers qualifications to perform the work indicated as required by the technical specification. Include certification of specific capabilities that would be required to comply with the technical specification (e.g., certified welders, electricians and registered engineers) and any ASME certification if the Manufacturer intends to manufacture equipment requiring ASME certification (vessels, heat exchangers, etc.). Provide examples of similar projects the Manufacturer has undertaken within the past five (5) years, including scope of work and general descriptions of each project. Equipment Description: Provide equipment description, sketches or bulletins indicating performance characteristics, features of the equipment, controls and instrumentation, valves, dimensions, estimated weight of unit (empty and full), and auxiliaries furnished. Component Data Information: Provide standard component data sheets for ALL components to be provided by outside sources or manufacturers. Where product data must be specially prepared because standard printed data is not suitable for use, submit as shop drawings. Product data shall include manufacturer, model number, catalog cut sheets and data indicating performance characteristics (i.e. performance curves), features, controls, instrumentation, wiring diagrams, equipment dimensions, estimated weights, heat rejection load when operating, auxiliaries, specialties, or accessories furnished, roughing-in or anchor diagrams and templates, manufacturer's installation and operating instructions, service clearance requirements, materials and finishes of all components. Mark each copy to show applicable choices and options. Where printed, Product Data includes information on several products, some of which are not required, mark copies to indicate the applicable information. Detailed Fabrication Schedule: Providea detailed fabrication schedule including critical review milestones and allowable review period per milestone. Any materials required for testing shall also be included in the schedule. Start-up and training assistance shall be included in the overall schedule. Standard QC Procedures: The Manufacturer's standard Quality Control (QC) procedures, acceptance criteria, and inspection procedures for both Manufacturer assembled systems and job shop or Manufacturer assembled components. Seismic Requirements: Provide seismic calculations performed to meet requirements where equipment will be installed. Calculations shall be sealed bya PE registered in that state. Utility Consumption Requirements: Provide consumption calculations and data for all utilities required, including average, instantaneous and peak demand loads, and their relative frequencies. Specific Service Support Plan: Provide specific information regarding the manufacturers capability to respond to emergency service calls. Provide the quantity of available service technicians, including their discipline and their location and costs for warranty and non-warranty support. Spare Parts List: Provide manufacturers recommended spare parts list. Indicate part number and generic description of the equipment part and the manufacturer. Bill of Material: Providea bill of material that lists all the major components of the proposed system, including description, part number, manufacturer/vendor and quantity. Equipment Shop Drawings: Provide shop drawings for all custom equipment, including that supplied by but not manufactured by the Manufacturer, (i.e. pumps, filter housings, and heat exchangers). Provide scaled shop drawings for all vessels, skids and air-handling units. Include asa minimum the following information on drawings or diagrams: Dimensions Identification of products and materials included; material thickness, surface finishes, etc. Orientations and schedule of all connections, nozzles and appurtenances Pressure and temperature ratings Notation of dimensions established by field measurement Estimated weight of unit (shipping and operating) Clearances for access and service Submit shop drawings on sheets at least 8" x 11", but no larger than 30" x 42" and/or electronically. System P&IDs: Provide Process and Instrumentation Diagrams that are specific for each system and that indicate all valves, instruments, piping, equipment, I&C logic and other components that will be used on the systems. Completed Specification Data Sheets: Provide all completed data sheets referenced in the technical specification. Complete all fields identified as VS* (Vendor Specified), as well as indicating any fields where the specified data differs from the Manufacturer's offering. This work can be done by hand directly on the data sheets provided it is legible and easily understood. Functional Specification (FS): Provide detailed information on the control system functionality including sequences, set points, interlocks, alarms, user interfaces, component interfaces, reporting, security, data handling, control hardware and software, and any other information required to describe and configure the overall control system. Shipping and Assembly Drawings: Provide detailed drawings indicating the shipping configuration of each system, including location and type of all rigging points. If the piece of equipment will be shipped in sub-sections, the drawings shall clearly indicate the boundaries, dimensions and weights of the sections. Assembly drawings shall also be provided to indicate how the sub-sections will be re-joined, including all mating points and types of connections between systems. Provide dimensioned plan, elevation and section drawings, and isometric drawings as needed to clearly indicate this information. Factory Acceptance Testing (FAT) Procedure: Provide the Manufacturers FAT procedure incorporating the tests indicated in the equipment specification. As-Built and Certified Equipment Drawings: Provide certified drawings that reflect the as-built status for all drawings previously issued for review and approval. All drawings shall indicate the Owner's purchase order number, equipment item number, project number, description, National Board number when applicable, and manufacturer's serial number. Certified drawings shall be signed and dated by an authorized representative of the manufacturer of that component or system. Testing and Calibration Equipment Data: Provide calibration procedures and current NIST traceable calibration certifications for all instruments used for calibration or testing of systems, including pressure gauges used for hydrostatic tests. ASME Data:
944 | 230510 | HYDRONIC SYSTEM SPECIALTIES | 1.2 | SUBMITTALS | General | Product data for each item specified here-in.
943 | 230510 | HYDRONIC SYSTEM SPECIALTIES | 1.4 | EXTRA MATERIALS....................................................................................................................... 1 | Attic Stock | PART 2. - PRODUCTS.......................................................................................................................................... 1
946 | 230510 | HYDRONIC SYSTEM SPECIALTIES | 1.4 | EXTRA MATERIALS | Attic Stock | For each type of balancing valve and automatic flow control valve, provide flowmeter, probe, hoses, flow charts and carrying case. Turn over to Owner at system start-up/turnover.
947 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4 | SUBMITTALS................................................................................................................................... 2 | General | PART 2. - PRODUCTS.......................................................................................................................................... 3
948 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-1 | SUBMITTALS | General | Dimensions
958 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-1 | SUBMITTALS | General | Motor speed versus torque curve at 100 percent, 90 percent, and 80 percent rated voltage
957 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-10 | SUBMITTALS | General | Guaranteed efficiency and power factor at full load The following data shall be furnished for all motors 150 HP or larger and for all motors that have high inertia loads or acceleration times over eight (8) seconds at full voltage:
949 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-2 | SUBMITTALS | General | Nameplate rating
959 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-2 | SUBMITTALS | General | Load speed versus torque curve
950 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-3 | SUBMITTALS | General | Connection data if more than three leads are brought out to the terminal box
960 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-3 | SUBMITTALS | General | Motor current versus speed curve at 100 percent, 90 percent, and 80 percent rated voltage
951 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-4 | SUBMITTALS | General | Auxiliary devices such as thermal switch, temperature sensor, space heater
961 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-4 | SUBMITTALS | General | Motor inertia and load inertia
952 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-5 | SUBMITTALS | General | Bearings
962 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-5 | SUBMITTALS | General | Motor stall time (hot and cold)
953 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-6 | SUBMITTALS | General | Lubrication recommendations
963 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-6 | SUBMITTALS | General | Open circuit time constant
954 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-7 | SUBMITTALS | General | Parts list
964 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-7 | SUBMITTALS | General | No-damage thermal limit curve
955 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-8 | SUBMITTALS | General | Weight
965 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-8 | SUBMITTALS | General | Locked rotor power factor
956 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-9 | SUBMITTALS | General | Motor mounting details
966 | 230513 | LOW VOLTAGE INDUCTION MOTOR | 1.4.-9 | SUBMITTALS | Performance Data | A statement certifying that routine tests (ANSI C50.20 and NEMA) were within standard performance limits.
968 | 230535 | CRYOGENIC PIPING SPECIALTIES | 1.1 | SUBMITTALS | General | Provide complete submittal for approval of piping layout and design including all piping and piping specialty components.
971 | 230535 | CRYOGENIC PIPING SPECIALTIES | 3.6 | TRAINING | O&M Training And Demonstration | Train Owner's maintenance personnel on procedures and schedules related to start-up and shut-down, troubleshooting, servicing, and preventative maintenance of cryogenic system. Review data in Operating and Maintenance Manuals. Schedule training with Owner through the Engineer, with at least seven (7) days advance notice.
972 | 230540 _revised_905 | PUMPS | 1.4 | SUBMITTALS................................................................................................................................... 2 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
974 | 230540 _revised_905 | PUMPS | 1.4 | SUBMITTALS | General | Reference specification section 230010 Basic Mechanical requirements for submittal requirements in addition to those indicated in this section. 1.4.1. Completed Data Sheets The Vendor/Manufacturer shall complete all fields indicated as VS* (Vendor Specified) on the schdule, as well as correct/modify any other fields and values as required, and submit them with the initial bid, and as part of the final submittal documentation.
977 | 230575 | BREECHINGS, CHIMNEYS, AND STACKS | 1.1 | SUBMITTALS | Certificates | Certificates: Submit certificates of materials compliance with specified ASTM, UL and ASHRAE requirements, NFPA 54 National Fuel Gas Code, and NFPA 31 Installation of Oil-Burning Equipment Certificates: Submit Welders' Qualification Certificates. Certificates: Submit complete engineering report certifying that stacks meet the design wind and seismic loads.
979 | 230586 | WATER TREATMENT SYSTEM | 1.2 | EXTENDED MAINTENANCE SERVICES..................................................................................... 1 | Maintenance Data | PART 2. - PRODUCTS.......................................................................................................................................... 2
981 | 230586 | WATER TREATMENT SYSTEM | 1.2 | EXTENDED MAINTENANCE SERVICES | Maintenance Data | Agreement to Maintain: Provide an Agreement for Continued Service and Maintenance for water treatment system, for Owner's possible acceptance. Offer terms and conditions for furnishing continued testing and servicing, and including replacement of materials and equipment, for one-year period with option for renewal of Agreement by Owner.
983 | 230587 | PACKAGED BASIN SWEEPER SKID | 1.2 | WARRANTY..................................................................................................................................... 1 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 1
985 | 230587 | PACKAGED BASIN SWEEPER SKID | 1.2 | WARRANTY | Warranty | Agreement to Maintain: Providea one year warranty after installation.
987 | 230670 | VARIABLE FLOW REFRIGERANT SYSTEM | 1.3 | SUBMITTALS | Product Data | Product Data: Include rated capacities, furnished specialties, and accessories for each type of product indicated. Include performance data in terms of capacities, outlet velocities, static pressures, sound power characteristics, motor requirements, and electrical characteristics. Shop Drawings: Diagram power, signal, and control wiring. Distinguish between field and factory wiring. Samples for Initial Selection: For units with factory-applied color finishes. Field quality-control test reports
986 | 230670 | VARIABLE FLOW REFRIGERANT SYSTEM | 1.6 | WARRANTY..................................................................................................................................... 2 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 2
989 | 230670 | VARIABLE FLOW REFRIGERANT SYSTEM | 1.6 | WARRANTY | Warranty | The units shall be covered by the manufacturers limited warranty fora period of one (1) year parts and seven (7) year compressor to the original owner from date of installation.
991 | 230670 | VARIABLE FLOW REFRIGERANT SYSTEM | 3.5 | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain units.
993 | 230711 | COOLING TOWERS | 1.1 | SUBMITTAL REQUIREMENTS | General | Provide submittals in compliance with Section 230010[jcs1].
992 | 230711 | COOLING TOWERS | 1.3.-1.4 | SEQUENCING AND SCHEDULING............................................................................................... 1 | Warranty | WARRANTY & PERFORMANCE CERTIFICATION.................................................................... 1 PART 2. - PRODUCTS.......................................................................................................................................... 2
995 | 230810 | HUMIDIFIERS | 1.3 | SUBMITTALS | Product Data | Product Data: Include rated capacities, furnished specialties, and accessories for each type of product indicated. Include performance data in terms of capacities, pressure drops, absorption distances, heat losses and electrical characteristics. Shop Drawings: Diagram power, signal, and control wiring. Field quality-control test reports. Operation and Maintenance Data: Provide operation, and maintenance manuals.
1001 | 230835 | AIR COILS | 1.4 | SUBMITTALS | General | Submit shop drawings for all coils in compliance with Section 230010 requirements. Submittals shall include all performance data noted in schedules.
999 | 230835 | AIR COILS | 1.5 | WARRANTY..................................................................................................................................... 1 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 2
1002 | 230835 | AIR COILS | 1.5 | WARRANTY | Warranty | Air Coils shall be guaranteed to achievea minimum of the capacity indicated on the respective schedules and shall havea minimum one year parts and labor warranty for material or workmanship defects. Division 01 Warranty requirements apply to this section.
1005 | 230856 | AIR ROTATIONAL UNITS | 1.3 | BID REQUIREMENTS | Product Data | The bid data shall provide all technical information relevant to the product being provided, including but not limited to, all the information shown in the attached schedule(s). It is the responsibility of the supplier to highlight any variances the equipment has with the requirements of this specification. Information shall be provided in the same measurement units as indicated in the schedule(s). Product data shall also be included at time of bid, including dimensions, weights, capacities, component performance, electrical characteristics, casing construction details, section splits, gauges and material finishes. The bids shall provide independent fan curves for operating/design conditions [not fan tables], with specified operating/design points clearly plotted (include internal pressure drop calculation). The bids shall provide coil selection worksheets, clearly showing proper consideration for altitude, air density, glycol corrections and indicate coil tube fin and casing construction. The manufacturer shall submit preliminary manufacturers recommended installation instructions with bid. The manufacturer shall havea list of all exceptions to the specification at time of bid.
1006 | 230856 | AIR ROTATIONAL UNITS | 1.4 | SUBMITTALS | General | General: Refer to specifications 230010 and 230050 for additional requirements. Product data shall include dimensions, weights, capacities, certifications, component performance, electrical characteristics, casing construction details, wiring interconnections, gauges and material finishes. The submittal shall provide all technical information relevant to the product being provided, including but not limited to, all the information shown in the attached schedules and drawings(s). It is the responsibility of the supplier to highlight any variances the equipment has with the requirements of this specification whether or not pre-approval has been obtained. Information shall be provided in the same measurement units as indicated in the schedules and drawings(s). The submittal(s) shall provide independent fan curves for operating/design conditions [not fan tables], with specified operating/design points clearly plotted. The submittal(s) shall provide coil selection worksheets, clearly showing proper consideration for altitude, air density, glycol corrections and indicate coil tube fin and casing construction. The submittal(s) shall provide filter information, including: initial (clean) APD, final (dirty) APD, dust spot efficiency, final dust holding capacity, filter media description, filter frame details, and filter removal details. The manufacturer shall submit sound power levels for both air handling unit inlet, outlet and radiated at rated capacity. The manufacturer shall submit electrical requirements for power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring. The manufacturer shall submit the manufacturers recommended installation instructions. Provide drawings of unit arrangement with dimensions for system and sections including utility connections. Omission of any of the above information will cause shop drawings to be immediately returned without review.
1007 | 230856 | AIR ROTATIONAL UNITS | 1.5 | OPERATION AND MAINTENANCE DATA | O&M Manuals | The manufacturer shall submit operation and maintenance data under provisions of Section 230010. The manufacturer shall include instructions for lubrication, filter replacement, motor and drive replacement, spare parts lists, and wiring diagrams.
1003 | 230856 | AIR ROTATIONAL UNITS | 1.6 | WARRANTY.............................................................................................................................. 4 | Warranty | PART 2.- PRODUCTS.................................................................................................................................... 4
1008 | 230856 | AIR ROTATIONAL UNITS | 1.6 | WARRANTY | Warranty | A warranty shall be provided by the manufacturer for the air handling unit(s). Sub-Contractor shall assume manufacturers warranty in its entirety, as if the equipment had been purchased by the Sub-Contractor. It shall be the responsibility of the Sub-Contractor, during the term of the warranty, to respond to reports of evident malfunction or failure, as though the equipment had been furnished by him, conduct the necessary diagnostic efforts, and if the malfunction is deemed by him to be the manufacturers warranty liability, to so resolve this responsibility with the manufacturer as the Owners agent.
1009 | 230856 | AIR ROTATIONAL UNITS | 3.5 | EXTRA FILTER STOCK | Attic Stock | The manufacturer will provide one extra set of pre-filters for each air handling unit. Install new filters at completion of air handling system work, and prior to testing, adjusting, and balancing work. Obtain receipt from testing and balancing Sub-Contractor that new filters have been installed.
1010 | 230860 | FANS | 1.4 | WARRANTY..................................................................................................................................... 1 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 2
1012 | 230860 | FANS | 1.4 | WARRANTY | Warranty | Provide warranty in accordance with Section 230010.
1014 | 230910 | DUCTWORK ACCESSORIES | 1.4 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
1016 | 230910 | DUCTWORK ACCESSORIES | 1.4 | SUBMITTALS | Product Data | Product Data: For each type of product indicated. Shop Drawings: Indicate installation details in ductwork and other construction. Provide wiring diagrams.
1018 | 230910 | DUCTWORK ACCESSORIES | 3.3 | ADJUSTING AND CLEANING | Attic Stock | Adjusting: Adjust ductwork accessories for proper settings, and adjust for proper action. Extra Stock Furnish extra fusible links to Owner, one (1) link for every 10 installed of each temperature range; obtain receipt.
1019 | 230932 | AIR OUTLETS AND INLETS | 1.4 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
1020 | 230932 | AIR OUTLETS AND INLETS | 1.4 | SUBMITTALS | Product Data | Product Data: For each type of product indicated, include the following: Indicate materials of construction, finish, and mounting details; and performance data including throw and drop, static-pressure drop, accessories and noise ratings. It is the responsibility of any manufacturer providing submittals to verify in advance their performance criteria is similar to Basis of Design (BOD) manufacturer in the following criteria. General compatibility- style, construction, ceiling or wall integration, fastening, color and accessories. Performance: NC level shall be equal to or less than BOD Static and total pressure shall be equal to or less than BOD Isothermal throw data at 150/100/50 fpm shall be within plus or minus 5% of the BOD values for standard products. Air devices for labs and critical spaces shall be shown with cooling temperature differentials of 5/10/15 degrees and throws of 100/75/50/30 fpm. Data shall be presented by computerized selection software. Catalog charts and graphs are not acceptable unless the tabular data is rated within 10% of the BOD performance selected. Manufacturers not complying with all portions of requirements will be rejected and not subject to further review by the design professional.
1021 | 230932 | AIR OUTLETS AND INLETS | 3.4 | SPARE PARTS | Attic Stock | Furnish to Owner, with receipt, three operating keys for each type of air outlet and inlet that require them.
1025 | 230934 | LABORATORY CONTROL SYSTEM | 1.2 | WARRANTY..................................................................................................................................... 1 | Warranty | PRODUCTS.......................................................................................................................................... 1
1027 | 230934 | LABORATORY CONTROL SYSTEM | 1.2 | WARRANTY | Warranty | The Warranty shall commence upon the date of shipment and extend fora period of 60 months for all airflow control devices and 36 months for all other control system components. PRODUCTS
1028 | 230934 | LABORATORY CONTROL SYSTEM | 2.1.-2 | LABORATORY AIRFLOW CONTROL SYSTEM | O&M Manuals | Operation and maintenance manuals, including as-built wiring diagrams and component lists, shall be provided for each training attendee.
1030 | 230935 | AIR CURTAIN | 1.3 | SUBMITTALS | Product Data | Product Data: Include rated capacities, furnished specialties, and accessories for each type of product indicated. Include performance data in terms of capacities, pressure drops,and electrical characteristics. Shop Drawings: Diagram power, signal, and control wiring. Field quality-control test reports. Operation and Maintenance Data: Provide operation, and maintenance manuals.
1033 | 230971 | HVAC SEQUENCE OF CONTROL | 1.3 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS NOT APPLICABLE..................................................................................................... 1 PART 3. - SEQUENCE OF CONTROL................................................................................................................ 2
1034 | 230972 | PLANT UTILITIES SEQUENCE OF CONTROL | 1.3 | SUBMITTALS................................................................................................................................... 1 | General | PART 2. - PRODUCTS NOT USED.................................................................................................................. 1 PART 3. - SEQUENCE OF CONTROL................................................................................................................ 1
1035 | 230972 | PLANT UTILITIES SEQUENCE OF CONTROL | 1.3 | SUBMITTALS | General | The following sequences shall be augmented as necessary by the Controls contractor and submitted either as part of the controls submittal or asa separate functional requirements specification for approval by the Engineer and Owner prior to commencing any programming.
1036 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.6 | WARRANTIES AND GUARANTEES | Warranty | In addition to warranties called for in other sections of these specifications, work shall be guaranteed against defect due to faulty installation, manufacture, and component design. Warranties and guarantees shall be fora period of not less than one year, beginning on the later date of final acceptance by Owners Representative, or equipment start-up. Upon written notice from the Owners Representative or Engineer, promptly remedy, without cost to the Owners Representative, any defects occurring or discovered during the guarantee period.
1037 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.7 | SUBMITTALS | General | General Provide submittals of material or equipment in accordance with the Submittal Requirement Schedule at the end of this specification section. A submittal is required if an "X" is indicated for that column and item. Some specification sections have very specific submittal requirements, not indicated in this section, and therefore are indicated in that specific specification section. The Architect/Engineer reserves the right to withhold action on all shop drawing and product data submittals until the Construction Manager deliversa register of anticipated submittals for review and comment. The register must indicate (estimated) issue dates for all future submittals. Submittal dates should be linked to construction milestones factoring in product lead times. The Construction Manager should also indicate schedule impact if submittal response is outside of the allowable review period. The Architect/Engineer reserves the right to delay review of submittals that have no impact or bearing on the construction schedule. Acceptable Manufacturers Subject to compliance with the requirements of the individual specification sections, provide materials and equipment from the indicated manufacturers only. Submittals of material or equipment manufactured by other than those indicated will be returned. 1.7.1. Review Action The Contractor is responsible for all data and information on submittals, including quantities, sizes, dimensions, and compliance with the Drawings and Specifications. Checking by the Owners Representative is only for general conformance with the design concept of the project and general compliance with the information given in the Contract Documents. Any action shown is subject to the requirements of the Drawings and Specifications. Contractor is responsible for dimensions and quantities which shall be confirmed at the jobsite, and fabrication process and techniques of construction. Except for submittals for record, information for similar purposes, where action and return is required or requested, the Owners Representative will check each submittal, mark to indicate action taken, and return promptly. Compliance with specified characteristics is the Contractor's responsibility. 1.7.2. Shop Drawings Submit information, drawn to accurate scale. Highlight, encircle, or otherwise indicate deviations from the Contract Documents. Do not reproduce Contract Documents (unless authorized by the Owners Representative/Engineer) or copy standard information as the basis of Shop Drawings. Standard information prepared without specific reference to the Project are not considered Shop Drawings. Shop Drawings include fabrication and installation drawings, setting diagrams, schedules, patterns, templates and similar drawings, and directions for installation of anchorages. Include asa minimum the following information on drawings or diagrams: Dimensions Identification of products and materials included Compliance with specified standards Notation of coordination requirements Notation of dimensions established by field measurement Clearances for access and service 1.7.3. Product Data Collect Product Data intoa single submittal for each element of construction or system. Where Product Data must be specially prepared because standard printed data is not suitable for use, submit as Shop Drawings. Product Data Information: Includes catalog cuts, sketches, or bulletins indicating performance characteristics, features of equipment, controls, instrumentation, valving, equipment dimensions, materials of construction, estimated weight of unit (shipping, installed, and operating), heat rejection load when operating, auxiliaries, specialties, or accessories furnished, roughing-in or anchor diagrams and templates, manufacturer's installation instructions, service clearance requirements, standard color charts, and wiring diagrams. Schematic Drawings shall include elevation and plan views, and indicate all connections, attachments, and details to indicate field required general details of assembly, etc. Wiring diagrams shall detail wiring for power, signal, and control systems, differentiating between manufacturer- installed wiring and field-installed wiring. Mark each copy to show applicable choices and options. Where printed Product Data includes information on several products, some of which are not required, mark copies to indicate the applicable information. Include the following information with above product data: Manufacturer's printed recommendations Compliance with recognized trade association standards Compliance with recognized testing agency standards Application of testing agency labels and seals Notation of dimensions verified by field measurement Notation of coordination requirements
1039 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-1 | SUBMITTAL REQUIREMENTS | General | Show tabulations of each variable frequency controller. Include the following : - i. Type of enclosure. ii. Equipment weight. iii. Input power supply requirements (volts/phase/amps). iv. Output power characteristics. v. HP range of motors drive is capable of driving. vi. Short-circuit current rating (SCCR) of assembly. vii. Converter pulse rate. viii. Network communications I/O interface capabilities. ix. Specified filters.
1041 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-1 | SUBMITTAL REQUIREMENTS | General | Test procedures used.
1044 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-1 | SUBMITTAL REQUIREMENTS | General | A complete listing of all programming parameters.
1040 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-2 | SUBMITTAL REQUIREMENTS | Wiring Diagram | Schematic and Connection Wiring Diagrams : For power, signal, and control wiring for each installed variable frequency controller. Qualification Data: For qualified testing agency. Field Quality-Control Reports
1042 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-2 | SUBMITTAL REQUIREMENTS | General | Test results that comply with requirements.
1045 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-2 | SUBMITTAL REQUIREMENTS | General | Instructions on how to modify program settings, and modify the control program.
1043 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-3 | SUBMITTAL REQUIREMENTS | O&M Manuals | Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For each type of variable frequency controller include operation and maintenance manual. In addition to items specified in Division 01 Section "Operation and Maintenance Data", include the following:
1046 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-3 | SUBMITTAL REQUIREMENTS | General | Instructions on drive adjustment, trouble-shooting, and configuration.
1047 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-4 | SUBMITTAL REQUIREMENTS | General | Instructions on process tuning and system calibration.
1048 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-5 | SUBMITTAL REQUIREMENTS | General | Routine maintenance requirements for variable frequency controller and all related components.
1049 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.5.-6 | SUBMITTAL REQUIREMENTS | Warranty | Instructions on shutdown procedures and any special instructions for maintaining the warranty.
1050 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 1.8.-1 | WARRANTY | Warranty | Warranty Period : 12 months minimum, non-prorated warranty on all parts and labor. Warranty period shall begin on the date of project substantial completion or date the drives are put into service by factory trained personnel required for startup and accepted by the Buyer, whichever occurs later.
1052 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 3.9 | DEMONSTRATION | O&M Training And Demonstration | Subsequent to wire and cable hook-ups, energize VFDs and test functioning for compliance with project requirements. Where necessary, correct malfunctioning units, and then retest for compliance. Training: The VFD supplier shall provide complete on-site training for the Owner's operating, maintenance and engineering personnel. Include in bid all costs for this service including, but not limited to, travel, lodging, and copies of training material. The trainer shall be factory certified by the VFD manufacturer. This training shall bea minimum of two (4) hours. Include in the traininga complete description on Theory of Operation, Operating Procedures, Functional and Operating Characteristics of Specific Logic Boards, Troubleshooting, Repair and Preventative Maintenance. A complete operations and maintenance manual shall be furnished with the training presentation.
1053 | 260500 | BASIC ELECTRICAL REQUIREMENTS | 3.10 | REPORTS | Reports | After energizing VFDs, submit copies of reports for all tests indicated above for review by the Engineer.
1056 | 260519 | LOW VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES | 1.5 | SUBMITTALS................................................................................................................................... 2 | General | PART 2.- PRODUCTS........................................................................................................................................... 2
1058 | 260519 | LOW VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of product.
1061 | 260523 | CONTROL VOLTAGE ELECTRICAL POWER CABLES | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of product.
1065 | 260524 | RADIANT HEATING ELECTRIC CABLES AND CONTROLS | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of product. Include rated capacities, operating characteristics, furnished specialties, and accessories for each type of product indicated. Schedule heating capacity, length of cable, spacing, and electrical power requirement for each electric heating cable required. Shop Drawings: For each heating cable, include plans, sections, details, and attachments to other work. Include wiring diagrams for heating cable power, signal, and control wiring. Include panel information and details, wiring diagrams, load information, installation details. Operation and Maintenance Data: Provide heating cable and control system operation and maintenance manuals.
1063 | 260524 | RADIANT HEATING ELECTRIC CABLES AND CONTROLS | 1.9 | WARRANTY..................................................................................................................................... 3 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 3
1069 | 260524 | RADIANT HEATING ELECTRIC CABLES AND CONTROLS | 1.9 | WARRANTY | Special Warranty | Special Warranty: Manufacturer agrees to repair or replace electric heating cable that fails in materials or workmanship within specified warranty period. Warranty Period: 10 years from date of Substantial Completion.
1066 | 260524 | RADIANT HEATING ELECTRIC CABLES AND CONTROLS | 1.7.-1 | EXTRA MATERIALS | Attic Stock | The larger of 10% of the quantity installed or (2) Power Connection Kits
1067 | 260524 | RADIANT HEATING ELECTRIC CABLES AND CONTROLS | 1.7.-2 | EXTRA MATERIALS | Attic Stock | The larger of 10% of the quantity installed or (2) End Seal Kits
1068 | 260524 | RADIANT HEATING ELECTRIC CABLES AND CONTROLS | 1.7.-3 | EXTRA MATERIALS | Attic Stock | The larger of 10% of the quantity installed or (2) Thermostats
1073 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5 | SUBMITTALS............................................................................................................................ 3 | General | PART 2. - PRODUCTS................................................................................................................................... 3
1075 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5.-1 | SUBMITTALS | General | Grounding arrangements and connections for separately derived systems.
1081 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5.-1 | SUBMITTALS | O&M Manuals | Operation and Maintenance Data shall include instructions for periodic testing and inspection of grounding features at ground rings based on NETA MTS and NFPA 70B: a. Tests shall determine if ground-resistance or impedance values remain within specified maximums, and instructions shall recommend corrective action if values do not. b. Include recommended testing intervals.
1076 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5.-2 | SUBMITTALS | General | Ground electrodes.
1077 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5.-3 | SUBMITTALS | General | Ground ring conductors.
1078 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5.-4 | SUBMITTALS | General | Interconnection with building structural and foundation steel.
1080 | 260526 | GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS | 1.5.-6 | SUBMITTALS | O&M Manuals | Interconnection with lightning protection system. Qualification Data: For testing agency and the testing agency's field supervisor. Field quality control reports. Operation and Maintenance Data: For grounding system components to be included in emergency, operation, and maintenance manuals related to sensitive electronic equipment.
1102 | 260533 | RACEWAYS | 1.5 | SUBMITTALS | Product Data | Product Data: For surface raceways, wireways and fittings, floor boxes, hinged-cover enclosures, and cabinets.
1104 | 260534 | ELECTRICAL BOXES AND FITTINGS | 1.4 | SUBMITTAL REQUIREMENTS | Product Data | Product Data: For each type of product including but not limited to materials, finishes, separators and miscellaneous components. Shop Drawings: For floor boxes, custom enclosures and cabinets. Include plans, elevations, sections, and attachment details. Coordination Drawings: Dimensioned floor box, and other in-slab box(es), location drawings. Included dimensioned plans using architectural floor plans, furniture system(s) floor plans, and structural floor plans. Indicate location of known underground utilities or structures. Dimensioned handhole, and other in-grade box(es), location drawings. Included dimensioned plans using architectural site plans, civil site plans, and structural site plans. Indicate location of known underground utilities or structures. Product Certificates: For concrete and steel used in precast concrete handholes, as required by ASTM C 858 and comply with BGE requirements.
1107 | 260536 | CABLE TRAYS FOR ELECTRICAL SYSTEMS | 1.1 | SUBMITTALS | Shop Drawings | Shop Drawings: Layout floor plans and elevations showing cable tray system. Designate components and accessories including clamps, brackets, hanger rods, splice plate connectors, expansion joint assemblies, straight lengths, and fittings. Show accurately scaled components and spatial relationships to adjacent equipment. Show tray types, dimensions, and finishes. Factory Test Reports: Certified copies of factory test reports performed in conformance with NEMA Standard VE 1 on cable trays of types and size specified for this project.
1112 | 262416 | PANELBOARDS | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of panelboard, switching and overcurrent protective device, surge protection device, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: For each panelboard and related equipment, include: Dimensioned plans, elevations, sections, and details. Show tabulations of installed equipment features, and ratings. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. Detail bus configuration, current, and voltage ratings. Qualification Data: For qualified testing agency. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Panelboard Schedules: For installation in panelboards. Operation and Maintenance Data: For panelboards and components to include in emergency, operation, and maintenance manuals.
1113 | 262416 | PANELBOARDS | 1.7 | EXTRA MATERIALS | Attic Stock | Provide pint of touch up paint for every ten (10) panelboards installed. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. Keys: Two (2) spares for each type of panelboard cabinet lock.
1110 | 262416 | PANELBOARDS | 1.9 | WARRANTY..................................................................................................................................... 4 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 4
1114 | 262416 | PANELBOARDS | 1.9.-1 | WARRANTY | Warranty | Warranty Period : 18 months minimum Special Warranty: Manufacturers standard form in which manufacturer agrees to repair or replace surge protection devices that fail in materials or workmanship within specified warranty period.
1115 | 262416 | PANELBOARDS | 1.9.-1 | WARRANTY | Warranty | Warranty Period : 10 years minimum
1126 | 262500 | ENCLOSED BUS ASSEMBLIES | 1.7 | EXTRA MATERIALS | Attic Stock | Provide pint of touch up paint for every 50 feet of busway installed.
1118 | 262500 | ENCLOSED BUS ASSEMBLIES | 1.9 | WARRANTY..................................................................................................................................... 3 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 4
1120 | 262500 | ENCLOSED BUS ASSEMBLIES | 1.5.-1 | SUBMITTALS | Manufacturers Instructions | Show fabrication and installation details for enclosed bus assemblies. Include plans, elevations, and sections of components. Designate components and accessories, including clamps, brackets, hanger rods, connectors, straight lengths, and fittings.
1121 | 262500 | ENCLOSED BUS ASSEMBLIES | 1.5.-2 | SUBMITTALS | General | Indicate required clearances, method of field assembly, and location and size of each field connection.
1122 | 262500 | ENCLOSED BUS ASSEMBLIES | 1.5.-3 | SUBMITTALS | General | Detail connections to busway and busway components and devices.
1123 | 262500 | ENCLOSED BUS ASSEMBLIES | 1.5.-4 | SUBMITTALS | General | Detailed connections to other electrical equipment, such as switchboards, switchgear, motor control centers, and/or panelboards.
1124 | 262500 | ENCLOSED BUS ASSEMBLIES | 1.5.-5 | SUBMITTALS | General | Cable and conductor terminal sizes for bus and plug-in device terminations.
1125 | 262500 | ENCLOSED BUS ASSEMBLIES | 1.5.-6 | SUBMITTALS | Wiring Diagram | Wiring Diagrams : Power, signal, and control wiring. Qualification Data: For testing agency. Field quality-control reports. Operation and Maintenance Data: For enclosed bus assemblies to include in emergency, operation, and maintenance manuals.
1127 | 262500 | ENCLOSED BUS ASSEMBLIES | 1.9.-1 | WARRANTY | Warranty | Warranty Period : 12 months minimum from date of shipment Manufacturer shall agree to repair or replace all components that fail in materials or workmanship within specified warranty period. Warranty shall include all labor, material, and related expenses to correct failures and return system to full functionality.
1136 | 262726 | WIRING DEVICES | 1.5 | SUBMITTALS................................................................................................................................... 2 | General | PART 2. - PRODUCTS.......................................................................................................................................... 2
1138 | 262726 | WIRING DEVICES | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of product.
1142 | 262816 | ENCLOSED SWITCHES AND CIRCUIT BREAKERS | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of enclosure, switching and overcurrent protective device, surge protection device, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: For each enclosure and related equipment, include: Dimensioned plans, elevations, sections, and details. Show tabulations of installed equipment features, and ratings. Detail enclosure types and details including mounting and anchorage, environmental protection, knockouts, corner treatments, covers and doors, and gaskets. Detail bus configuration, current, and voltage ratings. Qualification Data: For qualified testing agency. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For equipment and components to include in emergency, operation, and maintenance manuals.
1143 | 262816 | ENCLOSED SWITCHES AND CIRCUIT BREAKERS | 1.7 | EXTRA MATERIALS | Attic Stock | Provide pint of touch up paint for every twenty-five (25) enclosures installed, but not less than pint of touch up paint. Furnish extra materials as indicated in related specification documents.
1140 | 262816 | ENCLOSED SWITCHES AND CIRCUIT BREAKERS | 1.9 | WARRANTY..................................................................................................................................... 3 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 4
1144 | 262816 | ENCLOSED SWITCHES AND CIRCUIT BREAKERS | 1.9.-1 | WARRANTY | Warranty | Warranty Period : 24 months minimum
1148 | 262913 | ENCLOSED CONTROLLERS | 1.4 | SUBMITTALS | Product Data | Product Data: For each type of enclosed controller, enclosure, switching and overcurrent protection, surge protection device, accessory, and component indicated. Include dimensions and manufacturers technical data on features, performance, electrical characteristics, performance, ratings, and finishes. Shop Drawings: For each enclosed controller. Include dimensioned plans, elevations, sections, details, and required clearances and service spaces around controller enclosures. Show tabulations of the following: Each installed unit's type and details. Factory-installed devices. Nameplate legends. Short-circuit current rating of integrated unit. Listed and labeled for integrated short-circuit current (withstand) rating of OCPDs in combination controllers by an NRTL acceptable to authorities having jurisdiction. Features, characteristics, ratings, and factory settings of individual OCPDs in combination controllers. Wiring Diagrams: For power, signal, and control wiring. Operation and Maintenance Data: For enclosed controllers to include in emergency, operation, and maintenance manuals. In addition to items specified in include the following: Routine maintenance requirements for enclosed controllers and installed components. Manufacturer's written instructions for testing and adjusting circuit breaker and MCP trip settings. Manufacturer's written instructions for setting field-adjustable overload relays. Manufacturer's written instructions for testing, adjusting, and reprogramming reduced-voltage solid- state controllers. Load-Current and List of Settings of Adjustable Overload Relays: Compile after motors have been installed, and arrange to demonstrate that switch settings for motor running overload protection suit actual motors to be protected. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Load-Current and List of Settings of Adjustable Overload Relays: Compile after motors have been installed, and arrange to demonstrate that switch settings for motor running overload protection suit actual motors to be protected. Load-Current and Overload-Relay Heater List: Compile after motors installation and arrange to demonstrate that selection of heaters suits actual motor nameplate full-load currents. Operation and Maintenance Data: For equipment and components to include in emergency, operation, and maintenance manuals. Routine maintenance requirements for enclosed controllers and installed components. Manufacturer's written instructions for testing and adjusting circuit breaker and MCP trip settings. Manufacturer's written instructions for setting field-adjustable overload relays. Manufacturer's written instructions for testing, adjusting, and reprogramming reduced-voltage solid- state controllers.
1149 | 262913 | ENCLOSED CONTROLLERS | 1.6 | EXTRA MATERIALS | Attic Stock | Provide pint of touch up paint for every twenty-five (25) enclosures installed, but not less than pint of touch up paint. Furnish extra materials as indicated in related specification documents. Indicating Lights: Two of each type and color installed. Auxiliary Contacts: Furnish one spare(s) for each size and type of magnetic controller installed. Power Contacts: Furnish three spares for each size and type of magnetic contactor installed.
1146 | 262913 | ENCLOSED CONTROLLERS | 1.8 | WARRANTY.......................................................................................................................... 5 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 5
1150 | 262913 | ENCLOSED CONTROLLERS | 1.8 | WARRANTY | Manufacturers Warranty | Manufacturers Warranty: Manufacturer agrees to repair or replace equipment and components that fail in materials or workmanship within specified warranty period. Warranty Period: 18 months minimum
1152 | 262913 | ENCLOSED CONTROLLERS | 3.8 | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train owner's maintenance personnel to adjust, operate, and maintain enclosed controllers.
1155 | 263323 | CENTRAL BATTERY INVERTERS | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of central battery equipment unit, include performance, electrical ratings, product data sheets, operating characteristics, battery warranty, input and output circuit breakers, integrated distribution panels, shipping and operating weights, self-diagnostic features, shipping splits, and furnished options, specialties, and accessories. Shop Drawings: For each type and rating of central battery equipment unit, include: Plans, elevations, sections, and mounting details. Details of equipment assemblies: indicate dimensions, weights, loads, required clearances, ventilation requirements, method of field assembly, components, and locations and size of each field connection. System one-line diagram, internal and interconnecting wiring; and diagrams for power, signal, and control wiring. Short-circuit current rating of inverter and overcurrent protective devices. Elevation, details, and legends of control and indication displays. Source quality control reports Informational Submittals: Coordination Drawings: Floor plans, drawn to scale, showing dimensioned layout, required working clearances, and required area above and around central battery equipment. Show central battery equipment layout and relationships between electrical components and adjacent structural and mechanical elements. Show support locations, type of support, and weight on each support. Indicate field measurements. Qualification Data: for installer and testing agency. Product Certificates: For each type of central battery equipment. Field-Quality Control Reports: Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For central battery inverter and components to include in emergency, operation, and maintenance manuals. Operation and Maintenance Data: For central battery equipment to include in emergency, operation, and maintenance manuals. o Manufacturer's written instructions for testing central battery equipment. o Manufacturer's written instructions for testing, adjusting, and reprogramming microprocessor control modules. o Manufacturer's written instructions for selecting and setting field-adjustable controls and status and alarm points o Manufacturers listed gallons of electrolyte per battery cell
1156 | 263323 | CENTRAL BATTERY INVERTERS | 1.7 | EXTRA MATERIALS | Attic Stock | Provide pint of touch up paint for every two (2) central battery inverters installed, but not less than one (1) pint. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. Deliver extra material to Owner. Keys: Two (2) spares for each type of inverter cabinet lock. Fuses: One for every 10 of each type and rating, but no fewer than 2 of each type. Cabinet Ventilation Filters: One complete set.
1153 | 263323 | CENTRAL BATTERY INVERTERS | 1.9 | WARRANTY..................................................................................................................................... 5 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 5
1157 | 263323 | CENTRAL BATTERY INVERTERS | 1.9.-1 | WARRANTY | Warranty | Warranty Period : Include the following warranty periods, from date of Substantial Completion: a. Central Battery Equipment (excluding Batteries): Two years. b. Premium VRLA Batteries: i. Full Warranty: One year. ii. Pro Rata: 19 years.
1167 | 263323 | CENTRAL BATTERY INVERTERS | 3.7 | DEMONSTRATION | O&M Training And Demonstration | Engagea factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain central battery equipment, and to use and reprogram microprocessor-based control, monitoring, and display functions.
1158 | 263323 | CENTRAL BATTERY INVERTERS | 3.5.-1 | FIELD QUALITY CONTROL | O&M Training And Demonstration | Functional test and demonstration of all functions, controls, indicators, sensors, and protective devices.
1170 | 263600 | TRANSFER SWITCHES | 1.5 | SUBMITTALS | Product Data | Product Data: For each type of transfer switch, accessory, and component indicated. Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, weights, and finishes. Shop Drawings: For each transfer switch, include: Dimensioned plans, elevations, sections, details, and required clearances and service spaces around transfer switch enclosures. Show connections between transfer switch, power sources, and load. Show interconnection wiring between transfer switches, annunciators, control panels, generators, and building monitoring systems. Qualification Data: For qualified testing agency. Field-Quality Control Reports Test procedures used. Test results that comply with requirements. Results of failed tests and corrective action taken to achieve test results that comply with requirements. Operation and Maintenance Data: For each type of transfer switch and components include operation and maintenance manual. In addition to items specified in Division 01 Section Operation and Maintenance Data, include the following: Features and operating sequences, both automatic and manual. List of all factory settings of relays; provide relay-setting and calibration instructions, including software, where applicable.
1171 | 263600 | TRANSFER SWITCHES | 1.7 | EXTRA MATERIALS | Attic Stock | Provide pint of touch-up paint for each transfer switch installed. Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents. Keys: Two (2) spares for each type of cabinet lock. Maintenance Tools: Any non-standard tools specific to equipment type
1168 | 263600 | TRANSFER SWITCHES | 1.9 | WARRANTY..................................................................................................................................... 4 | Warranty | PART 2. - PRODUCTS.......................................................................................................................................... 4
1172 | 263600 | TRANSFER SWITCHES | 1.9.-1 | WARRANTY | Warranty | Warranty period : Minimum 18 months from shipment or 12 months from start-up, whichever occurs later.
1173 | 263600 | TRANSFER SWITCHES | 1.9.-2 | WARRANTY | Warranty | The warranty shall be comprehensive. No deductibles shall be allowed for travel time, service hours, repair cost, etc., during the minimum noted warranty period listed above.
1175 | 263600 | TRANSFER SWITCHES | 3.7 | TRAINING AND DEMONSTRATION | O&M Training And Demonstration | Upon completion of installation of equipment, and after building circuitry has been energized with normal power source, perform training and demonstration. Demonstrate operating procedures and operational compliance to the Owner's personnel and provide written operating instructions with full explanation of all technical information. Coordinate ATS training requirements to occur in conjunction with the generator training requirements specified in 263213.16. Training shall include written documentation provided to the Owner containing condensed operating instructions describing manufacturers normal operation procedures for test-mode, automatic operation, and emergency operational checks, procedures, and precautions for manual operation of the transfer switch duringa failure of the power transfer mechanism.
1176 | 264113 | LIGHTNING PROTECTION SYSTEMS | 1.3 | SUBMITTALS | Product Data | Product Data: For each type of product indicated, for example: grounding down conductors, through roof/through wall assemblies, roof conductors, air terminals, accessories, and components required. Include dimensions, weights, and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes. Shop Drawings: Showing the type, size, and locations of grounding down conductors, through roof/through wall assemblies, roof conductors, and air terminals, indicating the extent of the system layout designed specifically for the building(s) or structures included in the contract drawings along with details of the products to be used in the installation. Shop drawings shall include indications for use of raceway, data on how concealment requirements will be met, and calculations required by NFPA 780 for bonding of grounded and isolated metal bodies. Shop drawings shall be submitted to the Architect and the Engineer for approval prior to commencement of the installation. If any departures from the contract drawings or submittal drawings covered below are deemed necessary by the Contractor, details of such departures and reasons therefore shall be submitted as soon as practical to the Architect/Engineer for approval. Certification and Qualification Data: For Lightning Protection Institute (LPI) Certified designer and installer. Upon request, submit evidence of such qualifications to the Engineer.
1180 | 264313 | SURGE PROTECTION FOR LOW-VOLTAGE ELECTRICAL POWER | 1.4 | SUBMITTALS | General | For Review/Approval the following information shall be submitted to the Engineer: Provide verification that the SPD complies with the required ANSI/UL 1449 4th Edition listing by Intertek (ETL), Underwriters Laboratories (UL) or other Nationally Recognized Testing Laboratories (NRTL). Compliance may be in the form ofa file number that can be verified on ETLs or ULs website or on any other NRTLs website, as long as the website contains the following information ata minimum: model number, SPD Type, system voltage, phases, modes of protection, Voltage Protection Rating (VPR), and Nominal Discharge Current (In). Electrical/mechanical drawings showing unit dimensions, weights, installation instruction details, and wiring configuration. Where applicable the following additional information shall be submitted to the engineer: Descriptive bulletins Product sheets
1181 | 264313 | SURGE PROTECTION FOR LOW-VOLTAGE ELECTRICAL POWER | 1.5 | QUALIFICATIONS | Qualification Data | The manufacturer of the assembly shall be the manufacturer of the major components within the assembly. For the equipment specified herein, the manufacturer shall be ISO 14001 and ISO 9001 or 9002 certified. The manufacturer of this equipment shall have produced similar electrical equipment fora minimum period of five (5) years. When requested by the Engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement. The SPD shall be compliant with the Restriction of Hazardous Substances (RoHS) Directive 201165/EU The SPD shall be UL 1449 current edition listed, 20kA in Type 1 or Type 2 for use in UL96A systems.
1179 | 264313 | SURGE PROTECTION FOR LOW-VOLTAGE ELECTRICAL POWER | 1.7 | OPERATION AND MAINTENANCE MANUALS....................................................................... 2 | O&M Manuals | PART 2 - PRODUCTS........................................................................................................................................... 2
1182 | 264313 | SURGE PROTECTION FOR LOW-VOLTAGE ELECTRICAL POWER | 1.7 | OPERATION AND MAINTENANCE MANUALS | O&M Manuals | Operation and maintenance manuals shall be provided with each SPD shipped.
1183 | 264313 | SURGE PROTECTION FOR LOW-VOLTAGE ELECTRICAL POWER | 3.4 | WARRANTY | Warranty | The manufacturer shall providea full fifteen (10) year warranty from the date of shipment against any SPD part failure when installed in compliance with manufacturer's written instructions and any applicable national or local code.
1187 | 409010 | BASIC INSTRUMENTATION AND CONTROL REQUIREMENTS | 1.7 | WARRANTIES AND GUARANTEES | Warranty | In addition to warranties called for in other sections of these specifications, work shall be guaranteed against defect due to faulty installation. Warranties and guarantees shall be fora period of not less than one year, beginning on the later date of final acceptance by Owner, or equipment start-up. Upon written notice from the Owner or Owners Representative, promptly remedy, without cost to the Owner, any defects occurring or discovered during the guarantee period.
1188 | 409010 | BASIC INSTRUMENTATION AND CONTROL REQUIREMENTS | 1.8 | SUBMITTALS | General | General Provide submittals of material or equipment in accordance with the Submittal Requirement Schedule at the end of this specification section. Some sections have very specific submittals, not indicated in this section, and therefore are indicated ina specific specification section. Additional submittals are required if an "X" is indicated for that column and item. Acceptable Manufacturers Subject to compliance with the requirements of the individual specification sections, provide materials and equipment from the indicated manufacturers only. Submittals of material or equipment manufactured by other than those indicated may be returned. Procedures Coordination: Coordinate preparation and processing of submittals with performance of construction activities. Transmit each submittal sufficiently in advance of performance of related construction activities to avoid schedule delays. Coordinate each submittal with fabrication, purchasing, testing, delivery, other submittals, and related activities that requires sequential activity. Coordinate transmittal of different types of submittals for related elements of the work so processing will not be delayed by the need to review submittals concurrently for coordination. The Owner or Owner's Representative reserves the right to withhold action ona submittal requiring coordination with other submittals until related submittals are received. Processing: Allow sufficient review time so that installation will not be delayed asa result of the time required to process submittals, including time to resubmit. Allow two weeks for initial review. Allow additional time if processing must be delayed to permit coordination with subsequent submittals. The Owner or Owner's Representative will promptly advise the Contractor whena submittal being processed must be delayed for coordination. If an intermediate submittal is necessary, process the same as the initial submittal. Allow two weeks for reprocessing each submittal. No extension of contract time will be authorized because of failure to transmit submittals to the Owner or Owner's Representative sufficiently in advance of the work to permit processing. Preparation: Placea permanent label or title block on each submittal for identification. Indicate the name of the entity that prepared each submittal on the label or title block. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Contractor's review and approval markings and the action taken. Providea space approximately 4" x 5" on the label or beside the title block on Shop Drawings to record the Owner's or Owner's Representative review and approval markings and the action taken. Include the following information on the label or title block for processing and recording action taken. Project name Date Name and address of Owner Name and address of Engineer Name and address of Contractor Name and address of subcontractor Name and address of supplier Name of manufacturer Number and title of appropriate Specification Section Drawing number and detail references, as appropriate Transmittal: Package each submittal appropriately for transmittal and handling. Transmit each submittal from Contractor to Owner or Owner's Representative usinga transmittal form. Submittals received from sources other than the Contractor will be returned without action. Quantity: Submit electronic Portable Document Format (PDF) of each required submittal. The Owner will mark and return electronic copy with action taken and corrections or modifications required. Submittals shall be printed to.pdf, not printed as hardcopy and scanned to.pdf. Annotations to.pdf to clarify information, such as indicating specific options on an instrument cut sheet, should be done using editing tools in Adobe, Bluebeam, or comparable program, not hand-marked and scanned. The Engineer or Owner reserves the right to reject submittals without review if the.pdf is not readable or if pixilation occurs on zooming in, rendering enlarged content unreadable. Schedules: Project schedules indicating proposed work phases and sequences. Include in schedule asa minimum, approvals, equipment release, delivery, fabrication, equipment setting, startup, punch, and cleanup. Prepare and submita complete schedule of submittals. Coordinate the submittal schedule with the Contractor's construction schedule. Prepare the schedule in chronological order. Provide the following information: Scheduled date for the submittal Related Section number Submittal category Name of subcontractor Description of the part of the Work covered Scheduled date for resubmit Anticipated date for Engineer's final release or approval Distribution: Following response to initial submittal, print and distribute copies to subcontractors and other parties required to comply with submittal requirements. When revisions are made, distribute to the same parties. Delete parties from distribution when they have completed their assigned portion of the Work and are no longer involved in construction activities. Updating: Revise the schedule after each meeting or activity, where revisions have been recognized or made. Issue the updated schedule to all parties involved. 1.8.1. Review Action The Contractor is responsible for all data and information on submittals, including quantities, sizes, dimensions, and compliance with the Drawings and Specifications. Checking by the Owner or Owner's Representative is only for general conformance with the design concept of the project and general compliance with the information given in the Contract Documents. Any action shown is subject to the requirements of the Drawings and Specifications. Contractor is responsible for dimensions and quantities that shall be confirmed at the jobsite, and the fabrication process and techniques of construction. 1.8.2. Shop Drawings Submit information, drawn to accurate scale. Highlight, encircle, or otherwise indicate deviations from the Contract Documents. Do not reproduce Contract Documents or copy standard information as the basis of Shop Drawings. Standard information prepared without specific reference to the Project is not considered Shop Drawings. Shop Drawings include fabrication and installation drawings, setting diagrams, schedules, patterns, templates, and similar drawings. Include asa minimum the following information on drawings or diagrams: Dimensions Identification of products and materials included Compliance with specified standards Notation of coordination requirements Notation of dimensions established by field measurement if applicable Clearances for access and service 1.8.3. Product Data Collect Product Data intoa single submittal for each element of construction or system. Where Product Data must be specially prepared because standard printed data is not suitable for use, submit as Shop Drawings. Product Data Information: includes catalog cuts, sketches, or bulletins indicating performance characteristics, features of equipment, controls, instrumentation, equipment dimensions, materials of construction, estimated weights, heat rejection load when operating, auxiliaries, specialties, or accessories furnished, roughing-in or anchor diagrams and templates, manufacturer's installation instructions, service clearance requirements, standard color charts, and wiring diagrams. Mark each copy to show applicable choices and options. Where printed Product Data includes information on several products, some of which are not required, mark copies to indicate the applicable information. Include the following information with above product data: Manufacturer's printed recommendations Compliance with recognized trade association standards Compliance with recognized testing agency standards Application of testing agency labels and seals Notation of dimensions verified by field measurement Notation of coordination requirements Do not submit Product Data until compliance with requirements of the Contract Documents has been confirmed. Instrument Product Data and Format shall meet the following guidelines: 1. Cover sheet for each submittal, identifying the name of the client, name of the project, Vendors submittal ID, Vendors contact information, date, and purchase order number. 2. Submittals shall include the whole instrument assembly, for example, elements and transmitters, or valves, actuators and position switches. Multiple unrelated instrument types shall not be provided in the same document. 3. Instruments will be grouped by model number and will not contain more than one model number ina grouping. 4. A table for each group will contain the following fields ata minimum, tag number, P&ID, and any other optional important information such as line size, line specification, failure position, wetted elastomers, description, surface finish, etc. This table shall be sorted by Tag Number. 5. A model number code schedule that identifies each character in the model number and describes what the character represents, ora copy of the instrument cut sheet with each character in the model number highlighted on the order section. This must be provided for each unique model number. Any special characters that are not published by the manufacturer but exist in the model number shall be accompanied bya clear description as provided by manufacturer. Documentation of this description shall be provided in the form of official communications with manufacturer such as email or printed literature. 6. Instrumentation such as diaphragm valves, multiport valves, and RTD/thermowells, where the orientation and dimensions are more clearly described usinga drawing, shall be provided with the appropriate drawings. This drawing shall document sizes and label port numbers, w